## Commissioning Sheets
Commissioning Sheets
Controlworks Pty Ltd | Lismore Hospital | Project Number: PQ770
Point Name | Point ID | System Location | System | Point | Controller | I/O | Location | Hardware | Installed | Point to Point | Functional
Comms Room 3002
FCU-L3-01 | [7 empty] | ECB203
| FCU-L3-01-SW01 | Level-3 | FCU-L3-01 | Schedule | FCU-L3-01 | SW01 | Software | Software Point
| FCU-L3-01-DO1 | Level-3 | FCU-L3-01 | Fan Enable | FCU-L3-01 | DO1 | MSSB | 24VAC Relay
| FCU-L3-01-UI1 | Level-3 | FCU-L3-01 | Fan Status | FCU-L3-01 | UI1 | MSSB | CCS
| FCU-L3-01-UI2 | Level-3 | FCU-L3-01 | SA Temp | FCU-L3-01 | UI2 | SA Ductwork | PDIGR-TE200BE24B2
| FCU-L3-01-UI3 | Level-3 | FCU-L3-01 | Space Temp | FCU-L3-01 | UI3 | Space | PDITE-SENSORX0
| FCU-L3-01-UI4 | Level-3 | FCU-L3-01 | Dirty Filter | FCU-L3-01 | UI4 | Filter Box | AFS - 930.80222524
| FCU-L3-01-UO6 | Level-3 | FCU-L3-01 | CHW Valve | FCU-L3-01 | UO6 | FCU | CHWV Actuator
-
Lift Lobby and Corridor Areas 3C01
FCU-L3-02 | [7 empty] | ECB203
| FCU-L3-02-SW01 | Level-3 | FCU-L3-02 | Schedule | FCU-L3-02 | SW01 | Software | Software Point
| FCU-L3-02-DO1 | Level-3 | FCU-L3-02 | Fan Enable | FCU-L3-02 | DO1 | MSSB | 24VAC Relay
| OAF-L3-01-DO2 | Level-3 | OAF-L3-01 | OAF-L3-01 Fan Enable | OAF-L3-01 | DO2 | MSSB | 24VAC Relay
| FCU-L3-02-UI1 | Level-3 | FCU-L3-02 | Fan Status | FCU-L3-02 | UI1 | MSSB | CCS
| FCU-L3-02-UI2 | Level-3 | FCU-L3-02 | SA Temp | FCU-L3-02 | UI2 | SA Ductwork | PDIGR-TE200BE24B2
| FCU-L3-02-UI3 | Level-3 | FCU-L3-02 | RA Temp | FCU-L3-02 | UI3 | RA Ductwork | PDIGR-TE200BE24B2
| FCU-L3-02-UI4 | Level-3 | FCU-L3-02 | Dirty Filter | FCU-L3-02 | UI4 | Filter Box | AFS - 930.80222524
| OAF-L3-01-UI5 | Level-3 | OAF-L3-01 | OAF-L3-01 Status | OAF-L3-01 | UI5 | MSSB | CCS
| L3 Fire Signal-UI5 | Level-3 | L3 Fire Signal | Fire | L3 Fire Signal | UI5 | MSSB | 24VAC Relay
| FCU-L3-02-UO6 | Level-3 | FCU-L3-02 | CHW Valve | FCU-L3-02 | UO6 | FCU | CHWV Actuator
| FCU-L3-02-UO7 | Level-3 | FCU-L3-02 | HW Valve | FCU-L3-02 | UO7 | FCU | HHWV Actuator
-
Lift Lobby and Corridor Areas 3C01
FCU-L3-03 | [7 empty] | ECB203
| FCU-L3-03-SW01 | Level-3 | FCU-L3-03 | Schedule | FCU-L3-03 | SW01 | Software | Software Point
| FCU-L3-03-DO1 | Level-3 | FCU-L3-03 | Fan Enable | FCU-L3-03 | DO1 | MSSB | 24VAC Relay
| FCU-L3-03-UI1 | Level-3 | FCU-L3-03 | Fan Status | FCU-L3-03 | UI1 | MSSB | CCS
| FCU-L3-03-UI2 | Level-3 | FCU-L3-03 | SA Temp | FCU-L3-03 | UI2 | SA Ductwork | PDIGR-TE200BE24B2
| FCU-L3-03-UI3 | Level-3 | FCU-L3-03 | RA Temp | FCU-L3-03 | UI3 | RA Ductwork | PDIGR-TE200BE24B2
| FCU-L3-03-UI4 | Level-3 | FCU-L3-03 | Dirty Filter | FCU-L3-03 | UI4 | Filter Box | AFS - 930.80222524
| FCU-L3-03-UO6 | Level-3 | FCU-L3-03 | CHW Valve | FCU-L3-03 | UO6 | FCU | CHWV Actuator
| FCU-L3-03-UO7 | Level-3 | FCU-L3-03 | HW Valve | FCU-L3-03 | UO7 | FCU | HHWV Actuator
-
UPS Room 3E01
FCU-L3-04 | [7 empty] | ECB203
| FCU-L3-04-SW01 | Level-3 | FCU-L3-04 | Schedule | FCU-L3-04 | SW01 | Software | Software Point
| FCU-L3-04-DO1 | Level-3 | FCU-L3-04 | Fan Enable | FCU-L3-04 | DO1 | MSSB | 24VAC Relay
| FCU-L3-04-UI1 | Level-3 | FCU-L3-04 | Fan Status | FCU-L3-04 | UI1 | MSSB | CCS
| FCU-L3-04-UI2 | Level-3 | FCU-L3-04 | SA Temp | FCU-L3-04 | UI2 | SA Ductwork | PDIGR-TE200BE24B2
| FCU-L3-04-UI3 | Level-3 | FCU-L3-04 | RA Temp | FCU-L3-04 | UI3 | RA Ductwork | PDIGR-TE200BE24B2
| FCU-L3-04-UI4 | Level-3 | FCU-L3-04 | Dirty Filter | FCU-L3-04 | UI4 | Filter Box | AFS - 930.80222524
| FCU-L3-04-UO6 | Level-3 | FCU-L3-04 | CHW Valve | FCU-L3-04 | UO6 | FCU | CHWV Actuator
UO7
| FCU-L3-04-UO8 | Level-3 | FCU-L3-04 | Fan Speed | FCU-L3-04 | UO8 | FCU | Terminals
UPS Room 3E01
FCU-L3-05 | [7 empty] | ECB203
| FCU-L3-05-SW01 | Level-3 | FCU-L3-05 | Schedule | FCU-L3-05 | SW01 | Software | Software Point
| FCU-L3-05-DO1 | Level-3 | FCU-L3-05 | Fan Enable | FCU-L3-05 | DO1 | MSSB | 24VAC Relay
| FCU-L3-05-UI1 | Level-3 | FCU-L3-05 | Fan Status | FCU-L3-05 | UI1 | MSSB | CCS
| FCU-L3-05-UI2 | Level-3 | FCU-L3-05 | SA Temp | FCU-L3-05 | UI2 | SA Ductwork | PDIGR-TE200BE24B2
| FCU-L3-05-UI3 | Level-3 | FCU-L3-05 | RA Temp | FCU-L3-05 | UI3 | RA Ductwork | PDIGR-TE200BE24B2
| FCU-L3-05-UI4 | Level-3 | FCU-L3-05 | Dirty Filter | FCU-L3-05 | UI4 | Filter Box | AFS - 930.80222524
| GEF-L3-02-UI5 | Level-3 | GEF-L3-02 | GEF-L3-02 Status | GEF-L3-02 | UI5 | EA Ductwork | AFS - 930.80222524
| GEF-L3-03-UI6 | Level-3 | GEF-L3-03 | GEF-L3-03 Status | GEF-L3-03 | UI6 | EA Ductwork | AFS - 930.80222524
| FCU-L3-05-UO6 | Level-3 | FCU-L3-05 | CHW Valve | FCU-L3-05 | UO6 | FCU | CHWV Actuator
|  |  |  | Spare |  | UO7
| FCU-L3-05-UO8 | Level-3 | FCU-L3-05 | Fan Speed | FCU-L3-05 | UO8 | FCU | Terminals
Main Switch Room 3E02
FCU-L3-06 | [7 empty] | ECB203
| FCU-L3-06-SW01 | Level-3 | FCU-L3-06 | Schedule | FCU-L3-06 | SW01 | Software | Software Point
| FCU-L3-06-DO1 | Level-3 | FCU-L3-06 | Fan Enable | FCU-L3-06 | DO1 | MSSB | 24VAC Relay
| FCU-L3-06-UI1 | Level-3 | FCU-L3-06 | Fan Status | FCU-L3-06 | UI1 | MSSB | CCS
| FCU-L3-06-UI2 | Level-3 | FCU-L3-06 | SA Temp | FCU-L3-06 | UI2 | SA Ductwork | PDIGR-TE200BE24B2
| FCU-L3-06-UI3 | Level-3 | FCU-L3-06 | RA Temp | FCU-L3-06 | UI3 | RA Ductwork | PDIGR-TE200BE24B2
| FCU-L3-06-UI4 | Level-3 | FCU-L3-06 | Dirty Filter | FCU-L3-06 | UI4 | Filter Box | AFS - 930.80222524
| FCU-L3-06-UO6 | Level-3 | FCU-L3-06 | CHW Valve | FCU-L3-06 | UO6 | FCU | CHWV Actuator
|  |  |  | Spare |  | UO7
| FCU-L3-06-UO8 | Level-3 | FCU-L3-06 | Fan Speed | FCU-L3-06 | UO8 | FCU | Terminals
Level 3- Plant Areas 3H01/3H02
GEF-L3-01 | [7 empty] | VSD-GEF-L3-01
| GEF-L3-01-SW01 | Level-3 | GEF-L3-01 | Enable | GEF-L3-01 | SW01 | Level-3 | -
| GEF-L3-01-SW02 | Level-3 | GEF-L3-01 | Status | GEF-L3-01 | SW02 | Level-3 | -
| GEF-L3-01-SW03 | Level-3 | GEF-L3-01 | VSD Fault | GEF-L3-01 | SW03 | Level-3 | -
| GEF-L3-01-SW04 | Level-3 | GEF-L3-01 | VSD Speed Control | GEF-L3-01 | SW04 | Level-3 | -
Level 3 – UPS Room
GEF-L3-02 | [7 empty] | VSD-GEF-L3-02
| GEF-L3-02-SW01 | Level-3 | GEF-L3-02 | Enable | GEF-L3-02 | SW01 | Level-3 | -
| GEF-L3-02-SW02 | Level-3 | GEF-L3-02 | Status | GEF-L3-02 | SW02 | Level-3 | -
| GEF-L3-02-SW03 | Level-3 | GEF-L3-02 | VSD Fault | GEF-L3-02 | SW03 | Level-3 | -
| GEF-L3-02-SW04 | Level-3 | GEF-L3-02 | VSD Speed Control | GEF-L3-02 | SW04 | Level-3 | -
Level 3 – UPS Room
GEF-L3-03 | [7 empty] | VSD-GEF-L3-03
| GEF-L3-03-SW01 | Level-3 | GEF-L3-03 | Enable | GEF-L3-03 | SW01 | Level-3 | -
| GEF-L3-03-SW02 | Level-3 | GEF-L3-03 | Status | GEF-L3-03 | SW02 | Level-3 | -
| GEF-L3-03-SW03 | Level-3 | GEF-L3-03 | VSD Fault | GEF-L3-03 | SW03 | Level-3 | -
| GEF-L3-03-SW04 | Level-3 | GEF-L3-03 | VSD Speed Control | GEF-L3-03 | SW04 | Level-3 | -
MSB MISC | ECB600 |  |  | MSB Room |  |  |  | ECB600
| MSB MISC-UI1 | Site Boundaries | MSB MISC | Gas Meter 1 Pulse | MSB MISC | UI1 | Level-3 | Terminals
| MSB MISC-UI2 | Site Boundaries | MSB MISC | Gas Meter 2 Pulse | MSB MISC | UI2 | Level-3 | Terminals
| MSB MISC-UI3 | Site Boundaries | MSB MISC | Gas Meter 3 Pulse | MSB MISC | UI3 | Level-3 | Terminals
| MSB MISC-UI4 | Site Boundaries | MSB MISC | UV Steriliser 1 Hours Run Counter | MSB MISC | UI4 | Level-3 | Terminals
IO-DIM6-1 |  | L3 MSB |  | IO-DIM6-1 |  | UI5 |  | IO-DIM6
|  | L3 MSB |  | CB F1-1 N10 Open | MSB MISC |  |  | Terminals
|  | L3 MSB |  | CB F1-1 N10 Close | MSB MISC
|  | L3 MSB |  | CB F1-1 N10 Trip | MSB MISC
|  | L3 MSB |  | CB F1-9 N2 Open | MSB MISC
|  | L3 MSB |  | CB F1-9 N2 Close | MSB MISC
|  | L3 MSB |  | CB F1-9 N2 Trip | MSB MISC
IO-DIM6-2 |  | L3 MSB |  | IO-DIM6-2 |  | UI6 |  | IO-DIM6
|  | L3 MSB |  | CB F1-11 N1 Open | MSB MISC |  |  | Terminals
|  | L3 MSB |  | CB F1-11 N1 Close | MSB MISC
|  | L3 MSB |  | CB F1-11 N1 Trip | MSB MISC
|  | L3 MSB |  | CB F1-15 N7 Open | MSB MISC
|  | L3 MSB |  | CB F1-15 N7 Close | MSB MISC
|  | L3 MSB |  | CB F1-15 N7 Trip | MSB MISC
IO-DIM6-3 |  | L3 MSB |  | IO-DIM6-3 |  | UI7 |  | IO-DIM6
|  | L3 MSB |  | CB F2-1 N3 Open | MSB MISC |  |  | Terminals
|  | L3 MSB |  | CB F2-1 N3 Close | MSB MISC
|  | L3 MSB |  | CB F2-1 N3 Trip | MSB MISC
|  | L3 MSB |  | CB F2-3 N4 Open | MSB MISC
|  | L3 MSB |  | CB F2-3 N4 Close | MSB MISC
|  | L3 MSB |  | CB F2-3 N4 Trip | MSB MISC
IO-DIM6-4 |  | L3 MSB |  | IO-DIM6-4 |  | UI8 |  | IO-DIM6
|  | L3 MSB |  | CB F2-5 N5 Open | MSB MISC |  |  | Terminals
|  | L3 MSB |  | CB F2-5 N5 Close | MSB MISC
|  | L3 MSB |  | CB F2-5 N5 Trip | MSB MISC
|  | L3 MSB |  | CB F2-7 N6 Open | MSB MISC
|  | L3 MSB |  | CB F2-7 N6 Close | MSB MISC
|  | L3 MSB |  | CB F2-7 N6 Trip | MSB MISC
IO-DIM6-5 |  | L3 MSB |  | IO-DIM6-5 |  | UI9 |  | IO-DIM6
CB F2-9 Spare 160A Open |  | L3 MSB |  | CB F2-9 Spare 160A Open | MSB MISC |  |  | Terminals
CB F2-9 Spare 160A Close |  | L3 MSB |  | CB F2-9 Spare 160A Close | MSB MISC
CB F2-9 Spare 160A Trip |  | L3 MSB |  | CB F2-9 Spare 160A Trip | MSB MISC
CB F2-11 Spare 400A Open |  | L3 MSB |  | CB F2-11 Spare 400A Open | MSB MISC
CB F2-11 Spare 400A Close |  | L3 MSB |  | CB F2-11 Spare 400A Close | MSB MISC
CB F2-11 Spare 400A Trip |  | L3 MSB |  | CB F2-11 Spare 400A Trip | MSB MISC
IO-DIM6-6 |  | L3 MSB |  | IO-DIM6-6 |  | UI10 |  | IO-DIM6
CB F3-1 Spare 160A Open |  | L3 MSB |  | CB F3-1 Spare 160A Open | MSB MISC |  |  | Terminals
CB F3-1 Spare 160A Close |  | L3 MSB |  | CB F3-1 Spare 160A Close | MSB MISC
CB F3-1 Spare 160A Trip |  | L3 MSB |  | CB F3-1 Spare 160A Trip | MSB MISC
CB F3-2 Spare 160A Open |  | L3 MSB |  | CB F3-2 Spare 160A Open | MSB MISC
CB F3-2 Spare 160A Close |  | L3 MSB |  | CB F3-2 Spare 160A Close | MSB MISC
CB F3-2 Spare 160A Trip |  | L3 MSB |  | CB F3-2 Spare 160A Trip | MSB MISC
IO-DIM6-7 |  | L3 MSB |  | IO-DIM6-7 |  | UI11 |  | IO-DIM6
CB F3-5 Spare 250A Open |  | L3 MSB |  | CB F3-5 Spare 250A Open | MSB MISC |  |  | Terminals
CB F3-5 Spare 250A Close |  | L3 MSB |  | CB F3-5 Spare 250A Close | MSB MISC
CB F3-5 Spare 250A Trip |  | L3 MSB |  | CB F3-5 Spare 250A Trip | MSB MISC
CB F3-7 Spare 250A Open |  | L3 MSB |  | CB F3-7 Spare 250A Open | MSB MISC
CB F3-7 Spare 250A Close |  | L3 MSB |  | CB F3-7 Spare 250A Close | MSB MISC
CB F3-7 Spare 250A Trip |  | L3 MSB |  | CB F3-7 Spare 250A Trip | MSB MISC
IO-DIM6-8 |  | L3 MSB |  | IO-DIM6-8 |  | UI12 |  | IO-DIM6
CB F3-9 Spare 250A Open |  | L3 MSB |  | CB F3-9 Spare 250A Open | MSB MISC |  |  | Terminals
CB F3-9 Spare 250A Close |  | L3 MSB |  | CB F3-9 Spare 250A Close | MSB MISC
CB F3-9 Spare 250A Trip |  | L3 MSB |  | CB F3-9 Spare 250A Trip | MSB MISC
CB F3-11 Spare 400A Open |  | L3 MSB |  | CB F3-11 Spare 400A Open | MSB MISC
CB F3-11 Spare 400A Close |  | L3 MSB |  | CB F3-11 Spare 400A Close | MSB MISC
CB F3-11 Spare 400A Trip |  | L3 MSB |  | CB F3-11 Spare 400A Trip | MSB MISC
IO-DIM6-9 |  | L3 MSB |  | IO-DIM6-9 |  | UI13 |  | IO-DIM6
CB F3-14 Spare 630A Open |  | L3 MSB |  | CB F3-14 Spare 630A Open | MSB MISC |  |  | Terminals
CB F3-14 Spare 630A Close |  | L3 MSB |  | CB F3-14 Spare 630A Close | MSB MISC
CB F3-14 Spare 630A Trip |  | L3 MSB |  | CB F3-14 Spare 630A Trip | MSB MISC
CB F8-1 Spare 160A Open |  | L3 MSB |  | CB F8-1 Spare 160A Open | MSB MISC
CB F8-1 Spare 160A Close |  | L3 MSB |  | CB F8-1 Spare 160A Close | MSB MISC
CB F8-1 Spare 160A Trip |  | L3 MSB |  | CB F8-1 Spare 160A Trip | MSB MISC
IO-DIM6-10 |  | L3 MSB |  | IO-DIM6-10 |  | UI14 |  | IO-DIM6
CB F8-3 Spare 160A Open |  | L3 MSB |  | CB F8-3 Spare 160A Open | MSB MISC |  |  | Terminals
CB F8-3 Spare 160A Close |  | L3 MSB |  | CB F8-3 Spare 160A Close | MSB MISC
CB F8-3 Spare 160A Trip |  | L3 MSB |  | CB F8-3 Spare 160A Trip | MSB MISC
CB F8-7 Spare 160A Open |  | L3 MSB |  | CB F8-7 Spare 160A Open | MSB MISC
CB F8-7 Spare 160A Close |  | L3 MSB |  | CB F8-7 Spare 160A Close | MSB MISC
CB F8-7 Spare 160A Trip |  | L3 MSB |  | CB F8-7 Spare 160A Trip | MSB MISC
IO-DIM6-11 |  | L3 MSB |  | IO-DIM6-11 |  | UI15 |  | IO-DIM6
CB F8-9 E9 Open |  | L3 MSB |  | CB F8-9 E9 Open | MSB MISC |  |  | Terminals
CB F8-9 E9 Close |  | L3 MSB |  | CB F8-9 E9 Close | MSB MISC
CB F8-9 E9 Trip |  | L3 MSB |  | CB F8-9 E9 Trip | MSB MISC
CB F8-11 E8 Open |  | L3 MSB |  | CB F8-11 E8 Open | MSB MISC
CB F8-11 E8 Close |  | L3 MSB |  | CB F8-11 E8 Close | MSB MISC
CB F8-11 E8 Trip |  | L3 MSB |  | CB F8-11 E8 Trip | MSB MISC
IO-DIM6-12 |  | L3 MSB |  | IO-DIM6-12 |  | UI16 |  | IO-DIM6
CB F8-13 E25 Open |  | L3 MSB |  | CB F8-13 E25 Open | MSB MISC |  |  | Terminals
CB F8-13 E25 Close |  | L3 MSB |  | CB F8-13 E25 Close | MSB MISC
CB F8-13 E25 Trip |  | L3 MSB |  | CB F8-13 E25 Trip | MSB MISC
CB F11-1 Spare 250A Open |  | L3 MSB |  | CB F11-1 Spare 250A Open | MSB MISC
CB F11-1 Spare 250A Close |  | L3 MSB |  | CB F11-1 Spare 250A Close | MSB MISC
CB F11-1 Spare 250A Trip |  | L3 MSB |  | CB F11-1 Spare 250A Trip | MSB MISC
MSB MISC ECX420-1 |  |  |  | ECB600 Subnet |  |  |  | ECX420
IO-DIM6-13 |  | L3 MSB |  | IO-DIM6-13 | MSB MISC ECX420-1 | UI1 |  | IO-DIM6
CB F11-3 Spare 250A Open |  | L3 MSB |  | CB F11-3 Spare 250A Open | MSB MISC ECX420-1 |  |  | Terminals
CB F11-3 Spare 250A Close |  | L3 MSB |  | CB F11-3 Spare 250A Close | MSB MISC ECX420-1
CB F11-3 Spare 250A Trip |  | L3 MSB |  | CB F11-3 Spare 250A Trip | MSB MISC ECX420-1
CB F11-5 Spare 250A Open |  | L3 MSB |  | CB F11-5 Spare 250A Open | MSB MISC ECX420-1
CB F11-5 Spare 250A Close |  | L3 MSB |  | CB F11-5 Spare 250A Close | MSB MISC ECX420-1
CB F11-5 Spare 250A Trip |  | L3 MSB |  | CB F11-5 Spare 250A Trip | MSB MISC ECX420-1
IO-DIM6-14 |  | L3 MSB |  | IO-DIM6-14 |  | UI2 |  | IO-DIM6
CB F11-7 E24 Open |  | L3 MSB |  | CB F11-7 E24 Open | MSB MISC ECX420-1 |  |  | Terminals
CB F11-7 E24 Close |  | L3 MSB |  | CB F11-7 E24 Close | MSB MISC ECX420-1
CB F11-7 E24 Trip |  | L3 MSB |  | CB F11-7 E24 Trip | MSB MISC ECX420-1
CB F11-9 E23 Open |  | L3 MSB |  | CB F11-9 E23 Open | MSB MISC ECX420-1
CB F11-9 E23 Close |  | L3 MSB |  | CB F11-9 E23 Close | MSB MISC ECX420-1
CB F11-9 E23 Trip |  | L3 MSB |  | CB F11-9 E23 Trip | MSB MISC ECX420-1
IO-DIM6-15 |  | L3 MSB |  | IO-DIM6-15 |  | UI3 |  | IO-DIM6
CB F11-11 E13 Open |  | L3 MSB |  | CB F11-11 E13 Open | MSB MISC ECX420-1 |  |  | Terminals
CB F11-11 E13 Close |  | L3 MSB |  | CB F11-11 E13 Close | MSB MISC ECX420-1
CB F11-11 E13 Trip |  | L3 MSB |  | CB F11-11 E13 Trip | MSB MISC ECX420-1
CB F11-14 Spare 630A Open |  | L3 MSB |  | CB F11-14 Spare 630A Open | MSB MISC ECX420-1
CB F11-14 Spare 630A Close |  | L3 MSB |  | CB F11-14 Spare 630A Close | MSB MISC ECX420-1
CB F11-14 Spare 630A Trip |  | L3 MSB |  | CB F11-14 Spare 630A Trip | MSB MISC ECX420-1
IO-DIM6-16 |  | L3 MSB |  | IO-DIM6-16 |  | UI4 |  | IO-DIM6
CB F12-5 E17 Open |  | L3 MSB |  | CB F12-5 E17 Open | MSB MISC ECX420-1 |  |  | Terminals
CB F12-5 E17 Close |  | L3 MSB |  | CB F12-5 E17 Close | MSB MISC ECX420-1
CB F12-5 E17 Trip |  | L3 MSB |  | CB F12-5 E17 Trip | MSB MISC ECX420-1
CB F12-7 E16 Open |  | L3 MSB |  | CB F12-7 E16 Open | MSB MISC ECX420-1
CB F12-7 E16 Close |  | L3 MSB |  | CB F12-7 E16 Close | MSB MISC ECX420-1
CB F12-7 E16 Trip |  | L3 MSB |  | CB F12-7 E16 Trip | MSB MISC ECX420-1
IO-DIM6-17 |  | L3 MSB |  | IO-DIM6-17 |  | UI5 |  | IO-DIM6
CB F12-9 E15 Open |  | L3 MSB |  | CB F12-9 E15 Open | MSB MISC ECX420-1 |  |  | Terminals
CB F12-9 E15 Close |  | L3 MSB |  | CB F12-9 E15 Close | MSB MISC ECX420-1
CB F12-9 E15 Trip |  | L3 MSB |  | CB F12-9 E15 Trip | MSB MISC ECX420-1
CB F12-11 Spare 400A Open |  | L3 MSB |  | CB F12-11 Spare 400A Open | MSB MISC ECX420-1
CB F12-11 Spare 400A Close |  | L3 MSB |  | CB F12-11 Spare 400A Close | MSB MISC ECX420-1
CB F12-11 Spare 400A Trip |  | L3 MSB |  | CB F12-11 Spare 400A Trip | MSB MISC ECX420-1
IO-DIM6-18 |  | L3 MSB |  | IO-DIM6-18 |  | UI6 |  | IO-DIM6
CB F12-14 Spare 630A Open |  | L3 MSB |  | CB F12-14 Spare 630A Open | MSB MISC ECX420-1 |  |  | Terminals
CB F12-14 Spare 630A Close |  | L3 MSB |  | CB F12-14 Spare 630A Close | MSB MISC ECX420-1
CB F12-14 Spare 630A Trip |  | L3 MSB |  | CB F12-14 Spare 630A Trip | MSB MISC ECX420-1
CB F13-1 Spare 160A Open |  | L3 MSB |  | CB F13-1 Spare 160A Open | MSB MISC ECX420-1
CB F13-1 Spare 160A Close |  | L3 MSB |  | CB F13-1 Spare 160A Close | MSB MISC ECX420-1
CB F13-1 Spare 160A Trip |  | L3 MSB |  | CB F13-1 Spare 160A Trip | MSB MISC ECX420-1
IO-DIM6-19 |  | L3 MSB |  | IO-DIM6-19 |  | UI7 |  | IO-DIM6
CB F13-3 Spare 160A Open |  | L3 MSB |  | CB F13-3 Spare 160A Open | MSB MISC ECX420-1 |  |  | Terminals
CB F13-3 Spare 160A Close |  | L3 MSB |  | CB F13-3 Spare 160A Close | MSB MISC ECX420-1
CB F13-3 Spare 160A Trip |  | L3 MSB |  | CB F13-3 Spare 160A Trip | MSB MISC ECX420-1
CB F13-5 Spare 160A Open |  | L3 MSB |  | CB F13-5 Spare 160A Open | MSB MISC ECX420-1
CB F13-5 Spare 160A Close |  | L3 MSB |  | CB F13-5 Spare 160A Close | MSB MISC ECX420-1
CB F13-5 Spare 160A Trip |  | L3 MSB |  | CB F13-5 Spare 160A Trip | MSB MISC ECX420-1
IO-DIM6-20 |  | L3 MSB |  | IO-DIM6-20 |  | UI8 |  | IO-DIM6
CB F13-7 E14 Open |  | L3 MSB |  | CB F13-7 E14 Open | MSB MISC ECX420-1 |  |  | Terminals
CB F13-7 E14 Close |  | L3 MSB |  | CB F13-7 E14 Close | MSB MISC ECX420-1
CB F13-7 E14 Trip |  | L3 MSB |  | CB F13-7 E14 Trip | MSB MISC ECX420-1
CB F13-9 Spare 160A Open |  | L3 MSB |  | CB F13-9 Spare 160A Open | MSB MISC ECX420-1
CB F13-9 Spare 160A Close |  | L3 MSB |  | CB F13-9 Spare 160A Close | MSB MISC ECX420-1
CB F13-9 Spare 160A Trip |  | L3 MSB |  | CB F13-9 Spare 160A Trip | MSB MISC ECX420-1
IO-DIM6-21 |  | L3 MSB |  | IO-DIM6-21 |  | UI9 |  | IO-DIM6
CB F13-11 E22 Open |  | L3 MSB |  | CB F13-11 E22 Open | MSB MISC ECX420-1 |  |  | Terminals
CB F13-11 E22 Close |  | L3 MSB |  | CB F13-11 E22 Close | MSB MISC ECX420-1
CB F13-11 E22 Trip |  | L3 MSB |  | CB F13-11 E22 Trip | MSB MISC ECX420-1
CB F14-1 E21 Open |  | L3 MSB |  | CB F14-1 E21 Open | MSB MISC ECX420-1
CB F14-1 E21 Close |  | L3 MSB |  | CB F14-1 E21 Close | MSB MISC ECX420-1
CB F14-1 E21 Trip |  | L3 MSB |  | CB F14-1 E21 Trip | MSB MISC ECX420-1
IO-DIM6-22 |  | L3 MSB |  | IO-DIM6-22 |  | UI10 |  | IO-DIM6
CB F14-5 E12 Open |  | L3 MSB |  | CB F14-5 E12 Open | MSB MISC ECX420-1 |  |  | Terminals
CB F14-5 E12 Close |  | L3 MSB |  | CB F14-5 E12 Close | MSB MISC ECX420-1
CB F14-5 E12 Trip |  | L3 MSB |  | CB F14-5 E12 Trip | MSB MISC ECX420-1
CB F14-7 E11 Open |  | L3 MSB |  | CB F14-7 E11 Open | MSB MISC ECX420-1
CB F14-7 E11 Close |  | L3 MSB |  | CB F14-7 E11 Close | MSB MISC ECX420-1
CB F14-7 E11 Trip |  | L3 MSB |  | CB F14-7 E11 Trip | MSB MISC ECX420-1
IO-DIM6-23 |  | L3 MSB |  | IO-DIM6-23 |  | UI11 |  | IO-DIM6
CB F14-9 Spare 400A Open |  | L3 MSB |  | CB F14-9 Spare 400A Open | MSB MISC ECX420-1 |  |  | Terminals
CB F14-9 Spare 400A Close |  | L3 MSB |  | CB F14-9 Spare 400A Close | MSB MISC ECX420-1
CB F14-9 Spare 400A Trip |  | L3 MSB |  | CB F14-9 Spare 400A Trip | MSB MISC ECX420-1
CB F14-12 Spare 400A Open |  | L3 MSB |  | CB F14-12 Spare 400A Open | MSB MISC ECX420-1
CB F14-12 Spare 400A Close |  | L3 MSB |  | CB F14-12 Spare 400A Close | MSB MISC ECX420-1
CB F14-12 Spare 400A Trip |  | L3 MSB |  | CB F14-12 Spare 400A Trip | MSB MISC ECX420-1
IO-DIM6-24 |  | L3 MSB |  | IO-DIM6-24 |  | UI12 |  | IO-DIM6
CB F14-15 E10 Open |  | L3 MSB |  | CB F14-15 E10 Open | MSB MISC ECX420-1
CB F14-15 E10 Close |  | L3 MSB |  | CB F14-15 E10 Close | MSB MISC ECX420-1
CB F14-15 E10 Trip |  | L3 MSB |  | CB F14-15 E10 Trip | MSB MISC ECX420-1
Surge Diverter (Red) Fault |  | L3 MSB |  | Surge Diverter (Red) Fault | MSB MISC ECX420-1
Surge Diverter (White) Fault |  | L3 MSB |  | Surge Diverter (White) Fault | MSB MISC ECX420-1
Surge Diverter (Blue) Fault |  | L3 MSB |  | Surge Diverter (Blue) Fault | MSB MISC ECX420-1
MSB MISC ECX420-2 |  |  |  | ECB600 Subnet |  |  |  | ECX420
IO-DIM6-25 |  | L3 MSB |  | IO-DIM6-25 |  | UI1 |  | IO-DIM6
FH Diesel Water Pump Run Status |  | L3 MSB |  | FH Diesel Water Pump Run Status | Hydraulics
FH Diesel Water Pump Standby Status |  | L3 MSB |  | FH Diesel Water Pump Standby Status | Hydraulics
FH Diesel Water Pump Fault |  | L3 MSB |  | FH Diesel Water Pump Fault | Hydraulics
FH Electric Water Pump Run Status |  | L3 MSB |  | FH Electric Water Pump Run Status | Hydraulics
FH Electric Water Pump Standby Status |  | L3 MSB |  | FH Electric Water Pump Standby Status | Hydraulics
FH Electric Water Pump Fault |  | L3 MSB |  | FH Electric Water Pump Fault | Hydraulics
IO-DIM6-26 |  | L3 MSB |  | IO-DIM6-26 |  | UI2 |  | IO-DIM6
FS Diesel Water Pump Run Status |  | L3 MSB |  | FS Diesel Water Pump Run Status | Hydraulics
FS Diesel Water Pump Standby Status |  | L3 MSB |  | FS Diesel Water Pump Standby Status | Hydraulics
FS Diesel Water Pump Fault |  | L3 MSB |  | FS Diesel Water Pump Fault | Hydraulics
FS Electric Water Pump Run Status |  | L3 MSB |  | FS Electric Water Pump Run Status | Hydraulics
FS Electric Water Pump Standby Status |  | L3 MSB |  | FS Electric Water Pump Standby Status | Hydraulics
FS Electric Water Pump Fault |  | L3 MSB |  | FS Electric Water Pump Fault | Hydraulics
IO-DIM6-27 |  | L3 MSB |  | IO-DIM6-27 |  | UI3 |  | IO-DIM6
Fire Services Water Tank 1 High Level |  | L3 MSB |  | Fire Services Water Tank 1 High Level | Hydraulics
Fire Services Water Tank 1 Low Level |  | L3 MSB |  | Fire Services Water Tank 1 Low Level | Hydraulics
Fire Services Water Tank 1 Empty |  | L3 MSB |  | Fire Services Water Tank 1 Empty | Hydraulics
Fire Services Water Tank 2 High Level |  | L3 MSB |  | Fire Services Water Tank 2 High Level | Hydraulics
Fire Services Water Tank 2 Low Level |  | L3 MSB |  | Fire Services Water Tank 2 Low Level | Hydraulics
Fire Services Water Tank 2 Empty |  | L3 MSB |  | Fire Services Water Tank 2 Empty | Hydraulics
Hydraulics | ECB600 |  |  | MSSB Panel L3 |  |  |  | ECB600
Water Meter 1 Pulse | Hydraulics -UI1 | NZ F&B Actuator | Hydraulics | Water Meter 1 Pulse | Hydraulics | UI1 | Level-3 | Terminals
Water Meter 2 Pulse | Hydraulics -UI2 | NZ F&B Actuator | Hydraulics | Water Meter 2 Pulse | Hydraulics | UI2 | Level-3 | Terminals
Water Meter 3 Pulse | Hydraulics -UI3 | NZ F&B Actuator | Hydraulics | Water Meter 3 Pulse | Hydraulics | UI3 | Level-3 | Terminals
UV Steriliser 2 Hours Run Counter | Hydraulics -UI4 | NZ F&B Actuator | Hydraulics | UV Steriliser 2 Hours Run Counter | Hydraulics | UI4 | Level-3 | Terminals
IO-DIM6-28 |  | L3 MSB |  | IO-DIM6-28 |  | UI5 |  | IO-DIM6
Triplex Cold Water Pump 1 Run Status |  | L3 MSB |  | Triplex Cold Water Pump 1 Run Status | Hydraulics
Triplex Cold Water Pump 1 Standby Status |  | L3 MSB |  | Triplex Cold Water Pump 1 Standby Status | Hydraulics
Triplex Cold Water Pump 1 Fault |  | L3 MSB |  | Triplex Cold Water Pump 1 Fault | Hydraulics
Triplex Cold Water Pump 2 Run Status |  | L3 MSB |  | Triplex Cold Water Pump 2 Run Status | Hydraulics
Triplex Cold Water Pump 2 Standby Status |  | L3 MSB |  | Triplex Cold Water Pump 2 Standby Status | Hydraulics
Triplex Cold Water Pump 2 Fault |  | L3 MSB |  | Triplex Cold Water Pump 2 Fault | Hydraulics
IO-DIM6-29 |  | L3 MSB |  | IO-DIM6-29 |  | UI6 |  | IO-DIM6
Triplex Cold Water Pump 3 Run Status |  | L3 MSB |  | Triplex Cold Water Pump 3 Run Status | Hydraulics
Triplex Cold Water Pump 3 Standby Status |  | L3 MSB |  | Triplex Cold Water Pump 3 Standby Status | Hydraulics
Triplex Cold Water Pump 3 Fault |  | L3 MSB |  | Triplex Cold Water Pump 3 Fault | Hydraulics
HW Circ Pump 1 Run Status |  | L3 MSB |  | HW Circ Pump 1 Run Status | Hydraulics
HW Circ Pump 1 Pump Standby Status |  | L3 MSB |  | HW Circ Pump 1 Pump Standby Status | Hydraulics
HW Circ Pump 1 Pump Fault |  | L3 MSB |  | HW Circ Pump 1 Pump Fault | Hydraulics
IO-DIM6-30 |  | L3 MSB |  | IO-DIM6-30 |  | UI7 |  | IO-DIM6
HW Circ Pump 2 Run Status |  | L3 MSB |  | HW Circ Pump 2 Run Status | Hydraulics
HW Circ Pump 2 Pump Standby Status |  | L3 MSB |  | HW Circ Pump 2 Pump Standby Status | Hydraulics
HW Circ Pump 2 Pump Fault |  | L3 MSB |  | HW Circ Pump 2 Pump Fault | Hydraulics
LL Potable Water Tank 1 High Level |  | L3 MSB |  | LL Potable Water Tank 1 High Level | Hydraulics
LL Potable Water Tank 1 Low Level |  | L3 MSB |  | LL Potable Water Tank 1 Low Level | Hydraulics
LL Potable Water Tank 1 Empty |  | L3 MSB |  | LL Potable Water Tank 1 Empty | Hydraulics
IO-DIM6-31 |  | L3 MSB |  | IO-DIM6-31 |  | UI8 |  | IO-DIM6
LL Potable Water Tank 2 High Level |  | L3 MSB |  | LL Potable Water Tank 2 High Level | Hydraulics
LL Potable Water Tank 2 Low Level |  | L3 MSB |  | LL Potable Water Tank 2 Low Level | Hydraulics
LL Potable Water Tank 2 Empty |  | L3 MSB |  | LL Potable Water Tank 2 Empty | Hydraulics
Water Treatment St1 Filter 1 Run Status |  | L3 MSB |  | Water Treatment St1 Filter 1 Run Status | Hydraulics
Water Treatment St1 Filter 1 Backwash Status |  | L3 MSB |  | Water Treatment St1 Filter 1 Backwash Status | Hydraulics
Water Treatment St1 Filter 2 Run Status |  | L3 MSB |  | Water Treatment St1 Filter 2 Run Status | Hydraulics
IO-DIM6-32 |  | L3 MSB |  | IO-DIM6-32 |  | UI9 |  | IO-DIM6
Water Treatment St1 Filter 2 Backwash Status |  | L3 MSB |  | Water Treatment St1 Filter 2 Backwash Status | Hydraulics
Water Treatment St3 Filter 1 Run Status |  | L3 MSB |  | Water Treatment St3 Filter 1 Run Status | Hydraulics
Water Treatment St3 Filter 1 Fault |  | L3 MSB |  | Water Treatment St3 Filter 1 Fault | Hydraulics
Water Treatment St3 Filter 2 Run Status |  | L3 MSB |  | Water Treatment St3 Filter 2 Run Status | Hydraulics
Water Treatment St3 Filter 2 Fault |  | L3 MSB |  | Water Treatment St3 Filter 2 Fault | Hydraulics
Spare |  | L3 MSB |  | Spare | Hydraulics
IO-DIM6-33 |  | L3 MSB |  | IO-DIM6-33 |  | UI10 |  | IO-DIM6
Haemodialysis Water Treatment Sys1 Run Ststus |  | L3 MSB |  | Haemodialysis Water Treatment Sys1 Run Ststus | Hydraulics
Haemodialysis Water Treatment Sys1 Fault |  | L3 MSB |  | Haemodialysis Water Treatment Sys1 Fault | Hydraulics
Haemodialysis Water Treatment Sys2 Run Ststus |  | L3 MSB |  | Haemodialysis Water Treatment Sys2 Run Ststus | Hydraulics
Haemodialysis Water Treatment Sys2 Fault |  | L3 MSB |  | Haemodialysis Water Treatment Sys2 Fault | Hydraulics
Haemodialysis Water Treatment Sys3 Run Ststus |  | L3 MSB |  | Haemodialysis Water Treatment Sys3 Run Ststus | Hydraulics
Haemodialysis Water Treatment Sys3 Fault |  | L3 MSB |  | Haemodialysis Water Treatment Sys3 Fault | Hydraulics
IO-DIM6-34 |  | L3 MSB |  | IO-DIM6-34 |  | UI11 |  | IO-DIM6
TMV Monitor Hub Server Warning |  | L3 MSB |  | TMV Monitor Hub Server Warning | Hydraulics
TMV Monitor Hub Server Fault |  | L3 MSB |  | TMV Monitor Hub Server Fault | Hydraulics
Gas Interlock Open |  | L3 MSB |  | Gas Interlock Open | Hydraulics
Gas Interlock Close |  | L3 MSB |  | Gas Interlock Close | Hydraulics
|  | L3 MSB |  | 0 | Hydraulics
|  | L3 MSB |  | 0 | Hydraulics
IO-DIM6-35 |  | L3 MSB |  | IO-DIM6-35 |  | UI12 |  | IO-DIM6
DIFFS Diesel Water Pump Run Status |  | L3 MSB |  | DIFFS Diesel Water Pump Run Status | Hydraulics
DIFFS Diesel Water Pump Standby Status |  | L3 MSB |  | DIFFS Diesel Water Pump Standby Status | Hydraulics
DIFFS Diesel Water Pump Fault |  | L3 MSB |  | DIFFS Diesel Water Pump Fault | Hydraulics
DIFFS Electric Water Pump Run Status |  | L3 MSB |  | DIFFS Electric Water Pump Run Status | Hydraulics
DIFFS Electric Water Pump Standby Status |  | L3 MSB |  | DIFFS Electric Water Pump Standby Status | Hydraulics
DIFFS Electric Water Pump Fault |  | L3 MSB |  | DIFFS Electric Water Pump Fault | Hydraulics
IO-DIM6-36 |  | L3 MSB |  | IO-DIM6-36 |  | UI13 |  | IO-DIM6
DIFFS Water Tank 1 High Level |  | L3 MSB |  | DIFFS Water Tank 1 High Level | Hydraulics
DIFFS Water Tank 1 Low Level |  | L3 MSB |  | DIFFS Water Tank 1 Low Level | Hydraulics
DIFFS Water Tank 1 Empty |  | L3 MSB |  | DIFFS Water Tank 1 Empty | Hydraulics
DIFFS Water Tank 2 High Level |  | L3 MSB |  | DIFFS Water Tank 2 High Level | Hydraulics
DIFFS Water Tank 2 Low Level |  | L3 MSB |  | DIFFS Water Tank 2 Low Level | Hydraulics
DIFFS Water Tank 2 Empty |  | L3 MSB |  | DIFFS Water Tank 2 Empty | Hydraulics
Level 4
Comms Rooms 4108
FCU-L4-01 | [7 empty] | ECB203
Schedule | FCU-L4-01-SW01 | Level-4 | FCU-L4-01 | Schedule | FCU-L4-01 | SW01 | Software | Software Point
Fan Enable | FCU-L4-01-DO1 | Level-4 | FCU-L4-01 | Fan Enable | FCU-L4-01 | DO1 | MSSB | 24VAC Relay
GEF-L4-04 Fan Enable | GEF-L4-04-DO2 | Level-3 | GEF-L4-04 | GEF-L4-04 Fan Enable | GEF-L4-04 | DO2 | MSSB | 24VAC Relay
Fan Status | FCU-L4-01-UI1 | Level-4 | FCU-L4-01 | Fan Status | FCU-L4-01 | UI1 | MSSB | CCS
SA Temp | FCU-L4-01-UI2 | Level-4 | FCU-L4-01 | SA Temp | FCU-L4-01 | UI2 | SA Ductwork | PDIGR-TE200BE24B2
Space Temp | FCU-L4-01-UI3 | Level-4 | FCU-L4-01 | Space Temp | FCU-L4-01 | UI3 | Space | PDITE-SENSORX0
Dirty Filter | FCU-L4-01-UI4 | Level-4 | FCU-L4-01 | Dirty Filter | FCU-L4-01 | UI4 | Filter Box | AFS - 930.80222524
GEF-L4-04 Status | GEF-L4-04-UI5 | Level-4 | GEF-L4-04 | GEF-L4-04 Status | GEF-L4-04 | UI5 | MSSB | CCS
Fire | L4 Fire signal-UI5 | Level-4 | L4 Fire signal | Fire | L4 Fire signal | UI5 | MSSB | 24VAC Relay
CHW Valve | FCU-L4-01-UO6 | Level-4 | FCU-L4-01 | CHW Valve | FCU-L4-01 | UO6 | FCU | CHWV Actuator
Fan Speed | FCU-L4-01-UO8 | Level-4 | FCU-L4-01 | Fan Speed | FCU-L4-01 | UO8 | FCU | Terminals
Lift Lobby and Corridor Areas 4C07
FCU-L4-02 | [7 empty] | ECB203
Schedule | FCU-L4-02-SW01 | Level-4 | FCU-L4-02 | Schedule | FCU-L4-02 | SW01 | Software | Software Point
Fan Enable | FCU-L4-02-DO1 | Level-4 | FCU-L4-02 | Fan Enable | FCU-L4-02 | DO1 | MSSB | 24VAC Relay
OAF-L4-01 Fan Enable | OAF-L4-01-DO2 | Level-4 | OAF-L4-01 | OAF-L4-01 Fan Enable | OAF-L4-01 | DO2 | MSSB | 24VAC Relay
OAF-L4-02 Fan Enable | OAF-L4-02-DO3 | Level-4 | OAF-L4-02 | OAF-L4-02 Fan Enable | OAF-L4-02 | DO3 | MSSB | 24VAC Relay
Fan Status | FCU-L4-02-UI1 | Level-4 | FCU-L4-02 | Fan Status | FCU-L4-02 | UI1 | MSSB | CCS
SA Temp | FCU-L4-02-UI2 | Level-4 | FCU-L4-02 | SA Temp | FCU-L4-02 | UI2 | SA Ductwork | PDIGR-TE200BE24B2
RA Temp | FCU-L4-02-UI3 | Level-4 | FCU-L4-02 | RA Temp | FCU-L4-02 | UI3 | RA Ductwork | PDIGR-TE200BE24B2
Dirty Filter | FCU-L4-02-UI4 | Level-4 | FCU-L4-02 | Dirty Filter | FCU-L4-02 | UI4 | Filter Box | AFS - 930.80222524
OAF-L4-01 Status | OAF-L4-01-UI5 | Level-4 | OAF-L4-01 | OAF-L4-01 Status | OAF-L4-01 | UI5 | MSSB | CCS
OAF-L4-02 Status | OAF-L4-02-UI6 | Level-4 | OAF-L4-02 | OAF-L4-02 Status | OAF-L4-02 | UI6 | MSSB | CCS
CHW Valve | FCU-L4-02-UO6 | Level-4 | FCU-L4-02 | CHW Valve | FCU-L4-02 | UO6 | FCU | CHWV Actuator
HW Valve | FCU-L4-02-UO7 | Level-4 | FCU-L4-02 | HW Valve | FCU-L4-02 | UO7 | FCU | HHWV Actuator
Lift Lobby and Corridor Areas
FCU-L4-03 | [7 empty] | ECB203
Schedule | FCU-L4-03-SW01 | Level-4 | FCU-L4-03 | Schedule | FCU-L4-03 | SW01 | Software | Software Point
Fan Enable | FCU-L4-03-DO1 | Level-4 | FCU-L4-03 | Fan Enable | FCU-L4-03 | DO1 | MSSB | 24VAC Relay
Fan Status | FCU-L4-03-UI1 | Level-4 | FCU-L4-03 | Fan Status | FCU-L4-03 | UI1 | MSSB | CCS
SA Temp | FCU-L4-03-UI2 | Level-4 | FCU-L4-03 | SA Temp | FCU-L4-03 | UI2 | SA Ductwork | PDIGR-TE200BE24B2
RA Temp | FCU-L4-03-UI3 | Level-4 | FCU-L4-03 | RA Temp | FCU-L4-03 | UI3 | RA Ductwork | PDIGR-TE200BE24B2
Dirty Filter | FCU-L4-03-UI4 | Level-4 | FCU-L4-03 | Dirty Filter | FCU-L4-03 | UI4 | Filter Box | AFS - 930.80222524
CHW Valve | FCU-L4-03-UO6 | Level-4 | FCU-L4-03 | CHW Valve | FCU-L4-03 | UO6 | FCU | CHWV Actuator
HW Valve | FCU-L4-03-UO7 | Level-4 | FCU-L4-03 | HW Valve | FCU-L4-03 | UO7 | FCU | HHWV Actuator
UO8
-
Renal Department - Fluids 4093
FCU-L4-04 | [7 empty] | ECB203
Schedule | FCU-L4-04-SW01 | Level-4 | FCU-L4-04 | Schedule | FCU-L4-04 | SW01 | Software | Software Point
Fan Enable | FCU-L4-04-DO1 | Level-4 | FCU-L4-04 | Fan Enable | FCU-L4-04 | DO1 | MSSB | 24VAC Relay
Fan Status | FCU-L4-04-UI1 | Level-4 | FCU-L4-04 | Fan Status | FCU-L4-04 | UI1 | MSSB | CCS
SA Temp | FCU-L4-04-UI2 | Level-4 | FCU-L4-04 | SA Temp | FCU-L4-04 | UI2 | SA Ductwork | PDIGR-TE200BE24B2
RA Temp | FCU-L4-04-UI3 | Level-4 | FCU-L4-04 | RA Temp | FCU-L4-04 | UI3 | RA Ductwork | PDIGR-TE200BE24B2
Dirty Filter | FCU-L4-04-UI4 | Level-4 | FCU-L4-04 | Dirty Filter | FCU-L4-04 | UI4 | Filter Box | AFS - 930.80222524
Fire | L4 Fire signal-UI5 | Level-4 | L4 Fire signal | Fire | L4 Fire signal | UI5 | MSSB | 24VAC Relay
CHW Valve | FCU-L4-04-UO6 | Level-4 | FCU-L4-04 | CHW Valve | FCU-L4-04 | UO6 | FCU | CHWV Actuator
HW Valve | FCU-L4-04-UO7 | Level-4 | FCU-L4-04 | HW Valve | FCU-L4-04 | UO7 | FCU | HHWV Actuator
Renal - Main Waiting Area
FCU-L4-RN-01 | [7 empty] | ECB300
Schedule | FCU-L4-RN-01-SW01 | Level-4 | FCU-L4-RN-01 | Schedule | FCU-L4-RN-01 | SW01 | Software | Software Point
Fan Enable | FCU-L4-RN-01-UO1 | Level-4 | FCU-L4-RN-01 | Fan Enable | FCU-L4-RN-01 | UO1 | MSSB | 12VDC Relay
Fan Status | FCU-L4-RN-01-UI1 | Level-4 | FCU-L4-RN-01 | Fan Status | FCU-L4-RN-01 | UI1 | MSSB | CCS
SA Temp | FCU-L4-RN-01-UI2 | Level-4 | FCU-L4-RN-01 | SA Temp | FCU-L4-RN-01 | UI2 | SA Ductwork | PDIGR-TE200BE24B2
Space Temp | FCU-L4-RN-01-UI3 | Level-4 | FCU-L4-RN-01 | Space Temp | FCU-L4-RN-01 | UI3 | Space | PDITE-SENSORX0
Dirty Filter | FCU-L4-RN-01-UI4 | Level-4 | FCU-L4-RN-01 | Dirty Filter | FCU-L4-RN-01 | UI4 | Filter Box | AFS - 930.80222524
WZ Space Temp | AHU-L4-RN-WZ-UI5 | Level-4 | AHU-L4-RN-WZ | WZ Space Temp | AHU-L4-RN-WZ | UI5 | Space | PDITE-SENSORX0
CZ Space Temp 1 | AHU-L4-RN-CZ-UI6 | Level-4 | AHU-L4-RN-CZ | CZ Space Temp 1 | AHU-L4-RN-CZ | UI6 | Space | PDITE-SENSORX0
AH LED WZ-RN | AHU-L4-RN-WZ-UO4 | Level-4 | AHU-L4-RN-WZ | AH LED WZ-RN | AHU-L4-RN-WZ | UO4 | FCU | PDITE-SENSORX0
AH LED CZ1-RN | AHU-L4-RN-CZ-UO5 | Level-4 | AHU-L4-RN-CZ | AH LED CZ1-RN | AHU-L4-RN-CZ | UO5 | FCU | PDITE-SENSORX0
CHW Valve | FCU-L4-RN-01-UO6 | Level-4 | FCU-L4-RN-01 | CHW Valve | FCU-L4-RN-01 | UO6 | FCU | CHWV Actuator
HW Valve | FCU-L4-RN-01-UO7 | Level-4 | FCU-L4-RN-01 | HW Valve | FCU-L4-RN-01 | UO7 | FCU | HHWV Actuator
Renal - Meeting Room
FCU-L4-RN-02 | [7 empty] | ECB203
Schedule | FCU-L4-RN-02-SW01 | Level-4 | FCU-L4-RN-02 | Schedule | FCU-L4-RN-02 | SW01 | Software | Software Point
Fan Enable | FCU-L4-RN-02-DO1 | Level-4 | FCU-L4-RN-02 | Fan Enable | FCU-L4-RN-02 | DO1 | MSSB | 24VAC Relay
Fan Status | FCU-L4-RN-02-UI1 | Level-4 | FCU-L4-RN-02 | Fan Status | FCU-L4-RN-02 | UI1 | MSSB | CCS
SA Temp | FCU-L4-RN-02-UI2 | Level-4 | FCU-L4-RN-02 | SA Temp | FCU-L4-RN-02 | UI2 | SA Ductwork | PDIGR-TE200BE24B2
RA Temp | FCU-L4-RN-02-UI3 | Level-4 | FCU-L4-RN-02 | RA Temp | FCU-L4-RN-02 | UI3 | RA Ductwork | PDIGR-TE200BE24B2
Dirty Filter | FCU-L4-RN-02-UI4 | Level-4 | FCU-L4-RN-02 | Dirty Filter | FCU-L4-RN-02 | UI4 | Filter Box | AFS - 930.80222524
Small Drug Fridge Temp (Rm 4081 Clean Utility) | Fridges-UI5 | Level 5 | Fridges | Small Drug Fridge Temp (Rm 4081 Clean Utility) | Fridges | UI5 | Space | PDIGR-TE200BE24B2
Small Drug Fridge Fault (Rm 4081 Clean Utility) | Fridges-UI6 | Level 5 | Fridges | Small Drug Fridge Fault (Rm 4081 Clean Utility) | Fridges | UI6 | Space | Terminals
CHW Valve | FCU-L4-RN-02-UO6 | Level-4 | FCU-L4-RN-02 | CHW Valve | FCU-L4-RN-02 | UO6 | FCU | CHWV Actuator
HW Valve | FCU-L4-RN-02-UO7 | Level-4 | FCU-L4-RN-02 | HW Valve | FCU-L4-RN-02 | UO7 | FCU | HHWV Actuator
Renal - Group Training Room
FCU-L4-RN-03 | [7 empty] | ECB300
Schedule | FCU-L4-RN-03-SW01 | Level-4 | FCU-L4-RN-03 | Schedule | FCU-L4-RN-03 | SW01 | Software | Software Point
Fan Enable | FCU-L4-RN-03-UO1 | Level-4 | FCU-L4-RN-03 | Fan Enable | FCU-L4-RN-03 | UO1 | MSSB | 12VDC Relay
Fan Status | FCU-L4-RN-03-UI1 | Level-4 | FCU-L4-RN-03 | Fan Status | FCU-L4-RN-03 | UI1 | MSSB | CCS
SA Temp | FCU-L4-RN-03-UI2 | Level-4 | FCU-L4-RN-03 | SA Temp | FCU-L4-RN-03 | UI2 | SA Ductwork | PDIGR-TE200BE24B2
RA Temp | FCU-L4-RN-03-UI3 | Level-4 | FCU-L4-RN-03 | RA Temp | FCU-L4-RN-03 | UI3 | RA Ductwork | PDIGR-TE200BE24B2
Dirty Filter | FCU-L4-RN-03-UI4 | Level-4 | FCU-L4-RN-03 | Dirty Filter | FCU-L4-RN-03 | UI4 | Filter Box | AFS - 930.80222524
SZ Space Temp | AHU-L4-RN-SZ-UI5 | Level-4 | AHU-L4-RN-SZ | SZ Space Temp | AHU-L4-RN-SZ | UI5 | Space | PDITE-SENSORX0
CZ Space Temp 2 | AHU-L4-RN-CZ-UI6 | Level-4 | AHU-L4-RN-CZ | CZ Space Temp 2 | AHU-L4-RN-CZ | UI6 | Space | PDITE-SENSORX0
AH LED SZ-RN | AHU-L4-RN-SZ-UO4 | Level-4 | AHU-L4-RN-SZ | AH LED SZ-RN | AHU-L4-RN-SZ | UO4 | FCU | PDITE-SENSORX0
AH LED CZ2-RN | AHU-L4-RN-CZ-UO5 | Level-4 | AHU-L4-RN-CZ | AH LED CZ2-RN | AHU-L4-RN-CZ | UO5 | FCU | PDITE-SENSORX0
CHW Valve | FCU-L4-RN-03-UO6 | Level-4 | FCU-L4-RN-03 | CHW Valve | FCU-L4-RN-03 | UO6 | FCU | CHWV Actuator
HW Valve | FCU-L4-RN-03-UO7 | Level-4 | FCU-L4-RN-03 | HW Valve | FCU-L4-RN-03 | UO7 | FCU | HHWV Actuator
Renal - Staff Resource Room
FCU-L4-RN-04 | [7 empty] | ECB203
Schedule | FCU-L4-RN-04-SW01 | Level-4 | FCU-L4-RN-04 | Schedule | FCU-L4-RN-04 | SW01 | Software | Software Point
Fan Enable | FCU-L4-RN-04-DO1 | Level-4 | FCU-L4-RN-04 | Fan Enable | FCU-L4-RN-04 | DO1 | MSSB | 24VAC Relay
Fan Status | FCU-L4-RN-04-UI1 | Level-4 | FCU-L4-RN-04 | Fan Status | FCU-L4-RN-04 | UI1 | MSSB | CCS
SA Temp | FCU-L4-RN-04-UI2 | Level-4 | FCU-L4-RN-04 | SA Temp | FCU-L4-RN-04 | UI2 | SA Ductwork | PDIGR-TE200BE24B2
RA Temp | FCU-L4-RN-04-UI3 | Level-4 | FCU-L4-RN-04 | RA Temp | FCU-L4-RN-04 | UI3 | RA Ductwork | PDIGR-TE200BE24B2
Dirty Filter | FCU-L4-RN-04-UI4 | Level-4 | FCU-L4-RN-04 | Dirty Filter | FCU-L4-RN-04 | UI4 | Filter Box | AFS - 930.80222524
Large Drug Fridge Temp (Rm 4081 Clean Utility) | Fridges-UI5 | Level 5 | Fridges | Large Drug Fridge Temp (Rm 4081 Clean Utility) | Fridges | UI5 | Space | PDIGR-TE200BE24B2
Large Drug Fridge Fault (Rm 4081 Clean Utility) | Fridges-UI6 | Level 5 | Fridges | Large Drug Fridge Fault (Rm 4081 Clean Utility) | Fridges | UI6 | Space | Terminals
CHW Valve | FCU-L4-RN-04-UO6 | Level-4 | FCU-L4-RN-04 | CHW Valve | FCU-L4-RN-04 | UO6 | FCU | CHWV Actuator
HW Valve | FCU-L4-RN-04-UO7 | Level-4 | FCU-L4-RN-04 | HW Valve | FCU-L4-RN-04 | UO7 | FCU | HHWV Actuator
Emergency Department Support - Staff Room
FCU-L4-EDS-01 | [7 empty] | ECB300
Schedule | FCU-L4-EDS-01-SW01 | Level-4 | FCU-L4-EDS-01 | Schedule | FCU-L4-EDS-01 | SW01 | Software | Software Point
Fan Enable | FCU-L4-EDS-01-UO1 | Level-4 | FCU-L4-EDS-01 | Fan Enable | FCU-L4-EDS-01 | UO1 | MSSB | 12VDC Relay
Fan Status | FCU-L4-EDS-01-UI1 | Level-4 | FCU-L4-EDS-01 | Fan Status | FCU-L4-EDS-01 | UI1 | MSSB | CCS
SA Temp | FCU-L4-EDS-01-UI2 | Level-4 | FCU-L4-EDS-01 | SA Temp | FCU-L4-EDS-01 | UI2 | SA Ductwork | PDIGR-TE200BE24B2
RA Temp | FCU-L4-EDS-01-UI3 | Level-4 | FCU-L4-EDS-01 | RA Temp | FCU-L4-EDS-01 | UI3 | RA Ductwork | PDIGR-TE200BE24B2 + well
Dirty Filter | FCU-L4-EDS-01-UI4 | Level-4 | FCU-L4-EDS-01 | Dirty Filter | FCU-L4-EDS-01 | UI4 | Filter Box | AFS - 930.80222524
NZ Space Temp | AHU-L4-EDS-NZ-UI5 | Level-4 | AHU-L4-EDS-NZ | NZ Space Temp | AHU-L4-EDS-NZ | UI5 | Space | PDITE-SENSORX0
CZ Space Temp | AHU-L4-EDS-CZ-UI6 | Level-4 | AHU-L4-EDS-CZ | CZ Space Temp | AHU-L4-EDS-CZ | UI6 | Space | PDITE-SENSORX0
AH LED NZ-EDS | AHU-L4-EDS-NZ-UO4 | Level-4 | AHU-L4-EDS-NZ | AH LED NZ-EDS | AHU-L4-EDS-NZ | UO4 | FCU | PDITE-SENSORX0
AH LED CZ-EDS | AHU-L4-EDS-CZ-UO5 | Level-4 | AHU-L4-EDS-CZ | AH LED CZ-EDS | AHU-L4-EDS-CZ | UO5 | FCU | PDITE-SENSORX0
CHW Valve | FCU-L4-EDS-01-UO6 | Level-4 | FCU-L4-EDS-01 | CHW Valve | FCU-L4-EDS-01 | UO6 | FCU | CHWV Actuator
HW Valve | FCU-L4-EDS-01-UO7 | Level-4 | FCU-L4-EDS-01 | HW Valve | FCU-L4-EDS-01 | UO7 | FCU | HHWV Actuator
Emergency Department Support - Meeting Room
FCU-L4-EDS-02 | [7 empty] | ECB203
Schedule | FCU-L4-EDS-02-SW01 | Level-4 | FCU-L4-EDS-02 | Schedule | FCU-L4-EDS-02 | SW01 | Software | Software Point
Fan Enable | FCU-L4-EDS-02-DO1 | Level-4 | FCU-L4-EDS-02 | Fan Enable | FCU-L4-EDS-02 | DO1 | MSSB | 24VAC Relay
Fan Status | FCU-L4-EDS-02-UI1 | Level-4 | FCU-L4-EDS-02 | Fan Status | FCU-L4-EDS-02 | UI1 | MSSB | CCS
SA Temp | FCU-L4-EDS-02-UI2 | Level-4 | FCU-L4-EDS-02 | SA Temp | FCU-L4-EDS-02 | UI2 | SA Ductwork | PDIGR-TE200BE24B2
RA Temp | FCU-L4-EDS-02-UI3 | Level-4 | FCU-L4-EDS-02 | RA Temp | FCU-L4-EDS-02 | UI3 | RA Ductwork | PDIGR-TE200BE24B2
Dirty Filter | FCU-L4-EDS-02-UI4 | Level-4 | FCU-L4-EDS-02 | Dirty Filter | FCU-L4-EDS-02 | UI4 | Filter Box | AFS - 930.80222524
CHW Valve | FCU-L4-EDS-02-UO6 | Level-4 | FCU-L4-EDS-02 | CHW Valve | FCU-L4-EDS-02 | UO6 | FCU | CHWV Actuator
HW Valve | FCU-L4-EDS-02-UO7 | Level-4 | FCU-L4-EDS-02 | HW Valve | FCU-L4-EDS-02 | UO7 | FCU | HHWV Actuator
Mortuary – Office / Waiting / Viewing
FCU-L4-MO-01 | [7 empty] | ECB203
Schedule | FCU-L4-MO-01-SW01 | Level-4 | FCU-L4-MO-01 | Schedule | FCU-L4-MO-01 | SW01 | Software | Software Point
Fan Enable | FCU-L4-MO-01-DO1 | Level-4 | FCU-L4-MO-01 | Fan Enable | FCU-L4-MO-01 | DO1 | MSSB | 24VAC Relay
Fan Status | FCU-L4-MO-01-UI1 | Level-4 | FCU-L4-MO-01 | Fan Status | FCU-L4-MO-01 | UI1 | MSSB | CCS
SA Temp | FCU-L4-MO-01-UI2 | Level-4 | FCU-L4-MO-01 | SA Temp | FCU-L4-MO-01 | UI2 | SA Ductwork | PDIGR-TE200BE24B2
Space Temp ( Waiting) | FCU-L4-MO-01-UI3 | Level-4 | FCU-L4-MO-01 | Space Temp ( Waiting) | FCU-L4-MO-01 | UI3 | Space | PDITE-SENSORX0
Dirty Filter | FCU-L4-MO-01-UI4 | Level-4 | FCU-L4-MO-01 | Dirty Filter | FCU-L4-MO-01 | UI4 | Filter Box | AFS - 930.80222524
Body Hold Temp | FCU-L4-MO-01-UI5 | Level-4 | FCU-L4-MO-01 | Body Hold Temp | FCU-L4-MO-01 | UI5 | Freezer/Coldroom | PDIGR-TE200BE24B2
Body Hold Door Reed Sw | FCU-L4-MO-01-UI6 | Level-4 | FCU-L4-MO-01 | Body Hold Door Reed Sw | FCU-L4-MO-01 | UI6 | Freezer/Coldroom | Other
CHW Valve | FCU-L4-MO-01-UO6 | Level-4 | FCU-L4-MO-01 | CHW Valve | FCU-L4-MO-01 | UO6 | FCU | CHWV Actuator
HW Valve | FCU-L4-MO-01-UO7 | Level-4 | FCU-L4-MO-01 | HW Valve | FCU-L4-MO-01 | UO7 | FCU | HHWV Actuator
Mortuary - Autopsy Room
FCU-L4-MO-02 | [7 empty] | ECB300
Schedule | FCU-L4-MO-02-SW01 | Level-4 | FCU-L4-MO-02 | Schedule | FCU-L4-MO-02 | SW01 | Software | Software Point
Fan Enable | FCU-L4-MO-02-UO1 | Level-4 | FCU-L4-MO-02 | Fan Enable | FCU-L4-MO-02 | UO1 | MSSB | 12VDC Relay
Fan Status | FCU-L4-MO-02-UI1 | Level-4 | FCU-L4-MO-02 | Fan Status | FCU-L4-MO-02 | UI1 | MSSB | CCS
SA Temp | FCU-L4-MO-02-UI2 | Level-4 | FCU-L4-MO-02 | SA Temp | FCU-L4-MO-02 | UI2 | SA Ductwork | PDIGR-TE200BE24B2
Spare | FCU-L4-MO-02-UI3 | Level-4 | FCU-L4-MO-02 | Spare | FCU-L4-MO-02 | UI3
Dirty Filter | FCU-L4-MO-02-UI4 | Level-4 | FCU-L4-MO-02 | Dirty Filter | FCU-L4-MO-02 | UI4 | Filter Box | AFS - 930.80222524
Body Hold Refrigeration Unit Status | FCU-L4-MO-02-UI5 | Level-4 | FCU-L4-MO-02 | Body Hold Refrigeration Unit Status | FCU-L4-MO-02 | UI5 | Filter Box | AFS - 930.80222524
Body Hold Refrigeration Unit Fault | FCU-L4-MO-02-UI6 | Level-4 | FCU-L4-MO-02 | Body Hold Refrigeration Unit Fault | FCU-L4-MO-02 | UI6 | Filter Box | AFS - 930.80222524
Space Temp (Autopsy)/AH |  |  | Cat6 Ethernet Cable | RJ45 Connectors both sides | Space Temp |  | Space | EC - Vue Smart Sensor
Spare | FCU-L4-MO-02-UO5 | Level-4 | FCU-L4-MO-02 | Spare | FCU-L4-MO-02 | UO5
CHW Valve | FCU-L4-MO-02-UO6 | Level-4 | FCU-L4-MO-02 | CHW Valve | FCU-L4-MO-02 | UO6 | FCU | CHWV Actuator
HW Valve | FCU-L4-MO-02-UO7 | Level-4 | FCU-L4-MO-02 | HW Valve | FCU-L4-MO-02 | UO7 | FCU | HHWV Actuator
Fan Speed | FCU-L4-MO-02-UO8 | Level-4 | FCU-L4-MO-02 | Fan Speed | FCU-L4-MO-02 | UO8 | FCU | Terminals
Level 4 - Bridge Link
FCU-L4-BR-01 | [7 empty] | ECB203
Schedule | FCU-L4-BR-01-SW01 | Level-4 | FCU-L4-BR-01 | Schedule | FCU-L4-BR-01 | SW01 | Software | Software Point
Fan Enable | FCU-L4-BR-01-DO1 | Level-4 | FCU-L4-BR-01 | Fan Enable | FCU-L4-BR-01 | DO1 | MSSB | 24VAC Relay
Fan Status | FCU-L4-BR-01-UI1 | Level-4 | FCU-L4-BR-01 | Fan Status | FCU-L4-BR-01 | UI1 | MSSB | CCS
SA Temp | FCU-L4-BR-01-UI2 | Level-4 | FCU-L4-BR-01 | SA Temp | FCU-L4-BR-01 | UI2 | SA Ductwork | PDIGR-TE200BE24B2
RA Temp | FCU-L4-BR-01-UI3 | Level-4 | FCU-L4-BR-01 | RA Temp | FCU-L4-BR-01 | UI3 | RA Ductwork | PDIGR-TE200BE24B2
Dirty Filter | FCU-L4-BR-01-UI4 | Level-4 | FCU-L4-BR-01 | Dirty Filter | FCU-L4-BR-01 | UI4 | Filter Box | AFS - 930.80222524
CHW Valve | FCU-L4-BR-01-UO6 | Level-4 | FCU-L4-BR-01 | CHW Valve | FCU-L4-BR-01 | UO6 | FCU | CHWV Actuator
HW Valve | FCU-L4-BR-01-UO7 | Level-4 | FCU-L4-BR-01 | HW Valve | FCU-L4-BR-01 | UO7 | FCU | HHWV Actuator
Level 4 - Bridge Link
FCU-L4-BR-02 | [7 empty] | ECB203
Schedule | FCU-L4-BR-02-SW01 | Level-4 | FCU-L4-BR-02 | Schedule | FCU-L4-BR-02 | SW01 | Software | Software Point
Fan Enable | FCU-L4-BR-02-DO1 | Level-4 | FCU-L4-BR-02 | Fan Enable | FCU-L4-BR-02 | DO1 | MSSB | 24VAC Relay
Fan Status | FCU-L4-BR-02-UI1 | Level-4 | FCU-L4-BR-02 | Fan Status | FCU-L4-BR-02 | UI1 | MSSB | CCS
SA Temp | FCU-L4-BR-02-UI2 | Level-4 | FCU-L4-BR-02 | SA Temp | FCU-L4-BR-02 | UI2 | SA Ductwork | PDIGR-TE200BE24B2
RA Temp | FCU-L4-BR-02-UI3 | Level-4 | FCU-L4-BR-02 | RA Temp | FCU-L4-BR-02 | UI3 | RA Ductwork | PDIGR-TE200BE24B2
Dirty Filter | FCU-L4-BR-02-UI4 | Level-4 | FCU-L4-BR-02 | Dirty Filter | FCU-L4-BR-02 | UI4 | Filter Box | AFS - 930.80222524
NZ Space Temp | AHU-L4-RN-NZ-UI5 | Level-4 | AHU-L4-RN-NZ | NZ Space Temp | AHU-L4-RN-NZ | UI5 | Space | PDITE-SENSORX0
CHW Valve | FCU-L4-BR-02-UO6 | Level-4 | FCU-L4-BR-02 | CHW Valve | FCU-L4-BR-02 | UO6 | FCU | CHWV Actuator
HW Valve | FCU-L4-BR-02-UO7 | Level-4 | FCU-L4-BR-02 | HW Valve | FCU-L4-BR-02 | UO7 | FCU | HHWV Actuator
AH LED NZ-RN | AH LED NZ-RN |  |  | AH LED NZ-RN | AHU-L4-RN-NZ | UO8 | FCU | PDITE-SENSORX0
Photo Copy Room
Level 5
Emergency department
Isolation Room
FCU-L5-ISO-01 | [7 empty] | ECB600
Fan Enable Low Speed | FCU-L5-ISO-01-UO1 | Level-4 | FCU-L5-ISO-01 | Fan Enable Low Speed | FCU-L5-ISO-01 | UO1 | MSSB | 12VDC Relay
Fan Enable Medium Speed | FCU-L5-ISO-01-UO2 | Level-4 | FCU-L5-ISO-01 | Fan Enable Medium Speed | FCU-L5-ISO-01 | UO2 | MSSB | 12VDC Relay
Fan Enable High Speed | FCU-L5-ISO-01-UO3 | Level-4 | FCU-L5-ISO-01 | Fan Enable High Speed | FCU-L5-ISO-01 | UO3 | MSSB | 12VDC Relay
SA Fan Status | FCU-L5-ISO-01-UI1 | Level 5 | FCU-L5-ISO-01 | SA Fan Status | FCU-L5-ISO-01 | UI1 | MSSB | AFS - 930.80222524
SA Temp | FCU-L5-ISO-01-UI2 | Level 5 | FCU-L5-ISO-01 | SA Temp | FCU-L5-ISO-01 | UI2 | SA Ductwork | PDIGR-TE200BE24B2
Space Temp | FCU-L5-ISO-01-UI3 | Level 5 | FCU-L5-ISO-01 | Space Temp | FCU-L5-ISO-01 | UI3 | Space | PDITE-SENSORX0
Velocity | FCU-L5-ISO-01-UI4 | Level 5 | FCU-L5-ISO-01 | Velocity | FCU-L5-ISO-01 | UI4 | SA Velocity | QVM62.1
RA Humidity | FCU-L5-ISO-01-UI5 | Level 5 | FCU-L5-ISO-01 | RA Humidity | FCU-L5-ISO-01 | UI5 | RA Ductwork | QFM2160 Humidity
Dirty SA Pre-Filter | FCU-L5-ISO-01-UI6 | Level 5 | FCU-L5-ISO-01 | Dirty SA Pre-Filter | FCU-L5-ISO-01 | UI6 | Filter Box | AFS - 930.80222524
Dirty SA Deep Bed Filter | FCU-L5-ISO-01-UI7 | Level 5 | FCU-L5-ISO-01 | Dirty SA Deep Bed Filter | FCU-L5-ISO-01 | UI7 | Filter Box | AFS - 930.80222524
EA ISO Rm Heppa Filter Diff Press | FCU-L5-ISO-01-UI8 | Level 5 | FCU-L5-ISO-01 | EA ISO Rm Heppa Filter Diff Press | FCU-L5-ISO-01 | UI8 | Filter Press | QBM2030-5
EA ISO Toilet Heppa Filter Diff Press | FCU-L5-ISO-01-UI9 | Level 5 | FCU-L5-ISO-01 | EA ISO Toilet Heppa Filter Diff Press | FCU-L5-ISO-01 | UI9 | Filter Press | QBM2030-5
ISO Rm Diff Press | FCU-L5-ISO-01-UI10 | Level 5 | FCU-L5-ISO-01 | ISO Rm Diff Press | FCU-L5-ISO-01 | UI10 | Room DP | QBM2030-1U
Anteroom Diff Press | FCU-L5-ISO-01-UI11 | Level 5 | FCU-L5-ISO-01 | Anteroom Diff Press | FCU-L5-ISO-01 | UI11 | Room DP | QBM2030-1U
NZ Space Temp | AHU-L5-ED-2-NZ-UI12 | Level 5 | AHU-L5-ED-2-NZ | NZ Space Temp | AHU-L5-ED-2-NZ | UI12 | Space | PDITE-SENSORX0
Pressure Monitor |  |  | Cat6 Ethernet Cable | RJ45 Connectors both sides | Pressure Monitor |  | Space | EC - Vue Smart Sensor
CHW Valve | FCU-L5-ISO-01-UO4 | Level 5 | FCU-L5-ISO-01 | CHW Valve | FCU-L5-ISO-01 | UO4 | FCU | CHWV Actuator
HW Valve | FCU-L5-ISO-01-UO5 | Level 5 | FCU-L5-ISO-01 | HW Valve | FCU-L5-ISO-01 | UO5 | FCU | HHWV Actuator
Supply Damper | FCU-L5-ISO-01-UO6 | Level 5 | FCU-L5-ISO-01 | Supply Damper | FCU-L5-ISO-01 | UO6 | FCU | GDB161.1E
ISO Rm Audio Alarm | FCU-L5-ISO-01-UO7 | Level 5 | FCU-L5-ISO-01 | ISO Rm Audio Alarm | FCU-L5-ISO-01 | UO7 | FCU | 12VDC Relay
Anteroom Audio Alarm | FCU-L5-ISO-01-UO8 | Level 5 | FCU-L5-ISO-01 | Anteroom Audio Alarm | FCU-L5-ISO-01 | UO8 | FCU | 12VDC Relay
OAF-L5-02 Fan Enable | OAF-L5-02-UO9 | Level 5 | OAF-L5-02 | OAF-L5-02 Fan Enable | OAF-L5-02 | UO9 | MSSB | 12VDC Relay
AH LED NZ-ED-2 | AHU-L5-ED-2-NZ-UO10 | Level 5 | AHU-L5-ED-2-NZ | AH LED NZ-ED-2 | AHU-L5-ED-2-NZ | UO10 | FCU | PDITE-SENSORX0
Isolation Room
FCU-L5-ISO-02 | [7 empty] | ECB600
Fan Enable Low Speed | FCU-L4-BR-02-UO1 | Level-4 | FCU-L4-BR-02 | Fan Enable Low Speed | FCU-L4-BR-02 | UO1 | MSSB | 24VAC Relay
Fan Enable Medium Speed | FCU-L4-BR-02-UO2 | Level-4 | FCU-L4-BR-02 | Fan Enable Medium Speed | FCU-L4-BR-02 | UO2 | MSSB | 24VAC Relay
Fan Enable High Speed | FCU-L4-BR-02-UO3 | Level-4 | FCU-L4-BR-02 | Fan Enable High Speed | FCU-L4-BR-02 | UO3 | MSSB | 24VAC Relay
SA Fan Status | FCU-L5-ISO-01-UI1 | Level 5 | FCU-L5-ISO-01 | SA Fan Status | FCU-L5-ISO-01 | UI1 | MSSB | AFS - 930.80222524
SA Temp | FCU-L5-ISO-01-UI2 | Level 5 | FCU-L5-ISO-01 | SA Temp | FCU-L5-ISO-01 | UI2 | SA Ductwork | PDIGR-TE200BE24B2
Space Temp | FCU-L5-ISO-01-UI3 | Level 5 | FCU-L5-ISO-01 | Space Temp | FCU-L5-ISO-01 | UI3 | Space | PDITE-SENSORX0
Velocity | FCU-L5-ISO-01-UI4 | Level 5 | FCU-L5-ISO-01 | Velocity | FCU-L5-ISO-01 | UI4 | SA Velocity | QVM62.1
RA Humidity | FCU-L5-ISO-01-UI5 | Level 5 | FCU-L5-ISO-01 | RA Humidity | FCU-L5-ISO-01 | UI5 | RA Ductwork | QFM2160 Humidity
Dirty SA Pre-Filter | FCU-L5-ISO-01-UI6 | Level 5 | FCU-L5-ISO-01 | Dirty SA Pre-Filter | FCU-L5-ISO-01 | UI6 | Filter Box | AFS - 930.80222524
Dirty SA Deep Bed Filter | FCU-L5-ISO-01-UI7 | Level 5 | FCU-L5-ISO-01 | Dirty SA Deep Bed Filter | FCU-L5-ISO-01 | UI7 | Filter Box | AFS - 930.80222524
EA ISO Rm Heppa Filter Diff Press | FCU-L5-ISO-01-UI8 | Level 5 | FCU-L5-ISO-01 | EA ISO Rm Heppa Filter Diff Press | FCU-L5-ISO-01 | UI8 | Filter Press | QBM2030-5
EA ISO Toilet Heppa Filter Diff Press | FCU-L5-ISO-01-UI9 | Level 5 | FCU-L5-ISO-01 | EA ISO Toilet Heppa Filter Diff Press | FCU-L5-ISO-01 | UI9 | Filter Press | QBM2030-5
ISO Rm Diff Press | FCU-L5-ISO-01-UI10 | Level 5 | FCU-L5-ISO-01 | ISO Rm Diff Press | FCU-L5-ISO-01 | UI10 | Room DP | QBM2030-1U
Anteroom Diff Press | FCU-L5-ISO-01-UI11 | Level 5 | FCU-L5-ISO-01 | Anteroom Diff Press | FCU-L5-ISO-01 | UI11 | Room DP | QBM2030-1U
EZ Space Temp | AHU-L5-ED2-EZ-UI12 | Level 5 | AHU-L5-ED2-EZ | EZ Space Temp | AHU-L5-ED2-EZ | UI12 | Space | PDITE-SENSORX0
Pressure Monitor |  |  | Cat6 Ethernet Cable | RJ45 Connectors both sides | Pressure Monitor |  | Space | EC - Vue Smart Sensor
CHW Valve | FCU-L5-ISO-01-UO4 | Level 5 | FCU-L5-ISO-01 | CHW Valve | FCU-L5-ISO-01 | UO4 | FCU | CHWV Actuator
HW Valve | FCU-L5-ISO-01-UO5 | Level 5 | FCU-L5-ISO-01 | HW Valve | FCU-L5-ISO-01 | UO5 | FCU | HHWV Actuator
Supply Damper | FCU-L5-ISO-01-UO6 | Level 5 | FCU-L5-ISO-01 | Supply Damper | FCU-L5-ISO-01 | UO6 | FCU | GDB161.1E
ISO Rm Audio Alarm | FCU-L5-ISO-01-UO7 | Level 5 | FCU-L5-ISO-01 | ISO Rm Audio Alarm | FCU-L5-ISO-01 | UO7 | FCU | 12VDC Relay
Anteroom Audio Alarm | FCU-L5-ISO-01-UO8 | Level 5 | FCU-L5-ISO-01 | Anteroom Audio Alarm | FCU-L5-ISO-01 | UO8 | FCU | 12VDC Relay
AH LED EZ-ED-2 | AHU-L5-ED2-EZ-UO10 | Level 5 | AHU-L5-ED2-EZ | AH LED EZ-ED-2 | AHU-L5-ED2-EZ | UO10 | FCU | PDITE-SENSORX0
Comms Rooms 5108
FCU-L5-01 | [7 empty] | ECB203
Schedule | FCU-L5-01-SW01 | Level 5 | FCU-L5-01 | Schedule | FCU-L5-01 | SW01 | Software | Software Point
Fan Enable | FCU-L5-01-DO1 | Level 5 | FCU-L5-01 | Fan Enable | FCU-L5-01 | DO1 | MSSB | 24VAC Relay
Fan Status | FCU-L5-01-UI1 | Level 5 | FCU-L5-01 | Fan Status | FCU-L5-01 | UI1 | MSSB | CCS
SA Temp | FCU-L5-01-UI2 | Level 5 | FCU-L5-01 | SA Temp | FCU-L5-01 | UI2 | SA Ductwork | PDIGR-TE200BE24B2
Space Temp | FCU-L5-01-UI3 | Level 5 | FCU-L5-01 | Space Temp | FCU-L5-01 | UI3 | Space | PDITE-SENSORX0
Dirty Filter | FCU-L5-01-UI4 | Level 5 | FCU-L5-01 | Dirty Filter | FCU-L5-01 | UI4 | Filter Box | AFS - 930.80222524
Blood Fridge Fridge Temp (Rm 5063 Bay Pathology) | Fridges-UI5 | Level 5 | Fridges | Blood Fridge Fridge Temp (Rm 5063 Bay Pathology) | Fridges | UI5 | Space | PDIGR-TE200BE24B2
Blood Fridge Fridge Fault (Rm 5063 Bay Pathology) | Fridges-UI6 | Level 5 | Fridges | Blood Fridge Fridge Fault (Rm 5063 Bay Pathology) | Fridges | UI6 | Space | Terminals
CHW Valve | FCU-L5-01-UO6 | Level 5 | FCU-L5-01 | CHW Valve | FCU-L5-01 | UO6 | FCU | CHWV Actuator
Fan Speed | FCU-L5-01-UO8 | Level 5 | FCU-L5-01 | Fan Speed | FCU-L5-01 | UO8 | FCU | Terminals
Lift Lobby and Corridor Areas
FCU-L5-02 | [7 empty] | ECB203
Schedule | FCU-L5-02-SW01 | Level 5 | FCU-L5-02 | Schedule | FCU-L5-02 | SW01 | Software | Software Point
Fan Enable | FCU-L5-02-DO1 | Level 5 | FCU-L5-02 | Fan Enable | FCU-L5-02 | DO1 | MSSB | 24VAC Relay
OAF-L5-01 Fan Enable | OAF-L5-01-DO2 | Level 5 | OAF-L5-01 | OAF-L5-01 Fan Enable | OAF-L5-01 | DO2 | MSSB | 24VAC Relay
OAF-L5-02 Fan Enable | OAF-L5-02-DO3 | Level 5 | OAF-L5-02 | OAF-L5-02 Fan Enable | OAF-L5-02 | DO3 | MSSB | 24VAC Relay
Fan Status | FCU-L5-02-UI1 | Level 5 | FCU-L5-02 | Fan Status | FCU-L5-02 | UI1 | MSSB | CCS
SA Temp | FCU-L5-02-UI2 | Level 5 | FCU-L5-02 | SA Temp | FCU-L5-02 | UI2 | SA Ductwork | PDIGR-TE200BE24B2
RA Temp | FCU-L5-02-UI3 | Level 5 | FCU-L5-02 | RA Temp | FCU-L5-02 | UI3 | RA Ductwork | PDIGR-TE200BE24B2
Dirty Filter | FCU-L5-02-UI4 | Level 5 | FCU-L5-02 | Dirty Filter | FCU-L5-02 | UI4 | Filter Box | AFS - 930.80222524
OAF-L5-01 Status | OAF-L5-01-UI5 | Level 5 | OAF-L5-01 | OAF-L5-01 Status | OAF-L5-01 | UI5 | MSSB | CCS
OAF-L5-02 Status | OAF-L5-02-UI6 | Level 5 | OAF-L5-02 | OAF-L5-02 Status | OAF-L5-02 | UI6 | MSSB | CCS
CHW Valve | FCU-L5-02-UO6 | Level 5 | FCU-L5-02 | CHW Valve | FCU-L5-02 | UO6 | FCU | CHWV Actuator
HW Valve | FCU-L5-02-UO7 | Level 5 | FCU-L5-02 | HW Valve | FCU-L5-02 | UO7 | FCU | HHWV Actuator
Lift Lobby and Corridor Areas
FCU-L5-03 | [7 empty] | ECB203
Schedule | FCU-L5-03-SW01 | Level 5 | FCU-L5-03 | Schedule | FCU-L5-03 | SW01 | Software | Software Point
Fan Enable | FCU-L5-03-DO1 | Level 5 | FCU-L5-03 | Fan Enable | FCU-L5-03 | DO1 | MSSB | 24VAC Relay
Fan Status | FCU-L5-03-UI1 | Level 5 | FCU-L5-03 | Fan Status | FCU-L5-03 | UI1 | MSSB | CCS
SA Temp | FCU-L5-03-UI2 | Level 5 | FCU-L5-03 | SA Temp | FCU-L5-03 | UI2 | SA Ductwork | PDIGR-TE200BE24B2
RA Temp | FCU-L5-03-UI3 | Level 5 | FCU-L5-03 | RA Temp | FCU-L5-03 | UI3 | RA Ductwork | PDIGR-TE200BE24B2
Dirty Filter | FCU-L5-03-UI4 | Level 5 | FCU-L5-03 | Dirty Filter | FCU-L5-03 | UI4 | Filter Box | AFS - 930.80222524
Fire | L5 Fire-UI5 | Level-6 | FCU-L5-03 | Fire | L5 Fire | UI5 | MSSB | 24VAC Relay
CHW Valve | FCU-L5-03-UO6 | Level 5 | FCU-L5-03 | CHW Valve | FCU-L5-03 | UO6 | FCU | CHWV Actuator
HW Valve | FCU-L5-03-UO7 | Level 5 | FCU-L5-03 | HW Valve | FCU-L5-03 | UO7 | FCU | HHWV Actuator
Level 5 - Bridge Link
FCU-L5-BR-01 | [7 empty] | ECB203
Schedule | FCU-L5-BR-01-SW01 | Level 5 | FCU-L5-BR-01 | Schedule | FCU-L5-BR-01 | SW01 | Software | Software Point
Fan Enable | FCU-L5-BR-01-DO1 | Level 5 | FCU-L5-BR-01 | Fan Enable | FCU-L5-BR-01 | DO1 | MSSB | 24VAC Relay
Fan Status | FCU-L5-BR-01-UI1 | Level 5 | FCU-L5-BR-01 | Fan Status | FCU-L5-BR-01 | UI1 | MSSB | CCS
SA Temp | FCU-L5-BR-01-UI2 | Level 5 | FCU-L5-BR-01 | SA Temp | FCU-L5-BR-01 | UI2 | SA Ductwork | PDIGR-TE200BE24B2
RA Temp | FCU-L5-BR-01-UI3 | Level 5 | FCU-L5-BR-01 | RA Temp | FCU-L5-BR-01 | UI3 | RA Ductwork | PDIGR-TE200BE24B2
Dirty Filter | FCU-L5-BR-01-UI4 | Level 5 | FCU-L5-BR-01 | Dirty Filter | FCU-L5-BR-01 | UI4 | Filter Box | AFS - 930.80222524
CHW Valve | FCU-L5-BR-01-UO6 | Level 5 | FCU-L5-BR-01 | CHW Valve | FCU-L5-BR-01 | UO6 | FCU | CHWV Actuator
HW Valve | FCU-L5-BR-01-UO7 | Level 5 | FCU-L5-BR-01 | HW Valve | FCU-L5-BR-01 | UO7 | FCU | HHWV Actuator
Level 5 - Bridge Link
FCU-L5-BR-02 | [7 empty] | ECB203
Schedule | FCU-L5-BR-02-SW01 | Level 5 | FCU-L5-BR-02 | Schedule | FCU-L5-BR-02 | SW01 | Software | Software Point
Fan Enable | FCU-L5-BR-02-DO1 | Level 5 | FCU-L5-BR-02 | Fan Enable | FCU-L5-BR-02 | DO1 | MSSB | 24VAC Relay
Fan Status | FCU-L5-BR-02-UI1 | Level 5 | FCU-L5-BR-02 | Fan Status | FCU-L5-BR-02 | UI1 | MSSB | CCS
SA Temp | FCU-L5-BR-02-UI2 | Level 5 | FCU-L5-BR-02 | SA Temp | FCU-L5-BR-02 | UI2 | SA Ductwork | PDIGR-TE200BE24B2
RA Temp | FCU-L5-BR-02-UI3 | Level 5 | FCU-L5-BR-02 | RA Temp | FCU-L5-BR-02 | UI3 | RA Ductwork | PDIGR-TE200BE24B2
Dirty Filter | FCU-L5-BR-02-UI4 | Level 5 | FCU-L5-BR-02 | Dirty Filter | FCU-L5-BR-02 | UI4 | Filter Box | AFS - 930.80222524
|  | Level 5 |  |  |  | UI5
- |  | Level 5 |  | - |  | UI6 |  | -
CHW Valve | FCU-L5-BR-02-UO6 | Level 5 | FCU-L5-BR-02 | CHW Valve | FCU-L5-BR-02 | UO6 | FCU | CHWV Actuator
HW Valve | FCU-L5-BR-02-UO7 | Level 5 | FCU-L5-BR-02 | HW Valve | FCU-L5-BR-02 | UO7 | FCU | HHWV Actuator
Emergency Department - Consulting Rooms
FCU-L5-ED-01 | [7 empty] | ECB300
Schedule | FCU-L5-ED-01-SW01 | Level 5 | FCU-L5-ED-01 | Schedule | FCU-L5-ED-01 | SW01 | Software | Software Point
Fan Enable | FCU-L5-ED-01-UO1 | Level 5 | FCU-L5-ED-01 | Fan Enable | FCU-L5-ED-01 | UO1 | MSSB | 12VDC Relay
Fan Status | FCU-L5-ED-01-UI1 | Level 5 | FCU-L5-ED-01 | Fan Status | FCU-L5-ED-01 | UI1 | MSSB | CCS
SA Temp | FCU-L5-ED-01-UI2 | Level 5 | FCU-L5-ED-01 | SA Temp | FCU-L5-ED-01 | UI2 | SA Ductwork | PDIGR-TE200BE24B2
Spare | FCU-L5-ED-01-UI3 | Level 5 | FCU-L5-ED-01 | Spare | FCU-L5-ED-01 | UI3 | Space
Dirty Filter | FCU-L5-ED-01-UI4 | Level 5 | FCU-L5-ED-01 | Dirty Filter | FCU-L5-ED-01 | UI4 | Filter Box | AFS - 930.80222524
NZ Space Temp | AHU-L5-ED1-NZ-UI5 | Level 5 | AHU-L5-ED1-NZ | NZ Space Temp | AHU-L5-ED1-NZ | UI5 | Space | PDITE-SENSORX0
SZ Space Temp | AHU-L5-ED1-SZ-UI6 | Level 5 | AHU-L5-ED1-SZ | SZ Space Temp | AHU-L5-ED1-SZ | UI6 | Space | PDITE-SENSORX0
Small Drug Fridge Temp (Rm 5054 Clean Utility) | Fridges-UI7 | Level 5 | Fridges | Small Drug Fridge Temp (Rm 5054 Clean Utility) | Fridges | UI7 | Space | PDIGR-TE200BE24B2
Small Drug Fridge Fault (Rm 5054 Clean Utility) | Fridges-UI8 | Level 5 | Fridges | Small Drug Fridge Fault (Rm 5054 Clean Utility) | Fridges | UI8 | Space | Terminals
Small Drug Fridge Temp (Rm 5218 Consulting) | Fridges-UI9 | Level 5 | Fridges | Small Drug Fridge Temp (Rm 5218 Consulting) | Fridges | UI9 | Space | PDIGR-TE200BE24B2
Small Drug Fridge Fault (Rm 5218 Consulting) | Fridges-UI10 | Level 5 | Fridges | Small Drug Fridge Fault (Rm 5218 Consulting) | Fridges | UI10 | Space | Terminals
Space Temp (Consult Rm 5022) |  |  | Cat6 Ethernet Cable | RJ45 Connectors both sides | Space Temp |  | Space | EC - Vue Smart Sensor
AH LED NZ-ED-1 | AHU-L5-ED-1-NZ-UO4 | Level 5 | AHU-L5-ED-1-NZ | AH LED NZ-ED-1 | AHU-L5-ED-1-NZ | UO4 | FCU | PDITE-SENSORX0
AH LED SZ-ED-1 | AHU-L5-ED-1-SZ-UO5 | Level 5 | AHU-L5-ED-1-SZ | AH LED SZ-ED-1 | AHU-L5-ED-1-SZ | UO5 | FCU | PDITE-SENSORX0
CHW Valve | FCU-L5-ED-01-UO6 | Level 5 | FCU-L5-ED-01 | CHW Valve | FCU-L5-ED-01 | UO6 | FCU | CHWV Actuator
HW Valve | FCU-L5-ED-01-UO7 | Level 5 | FCU-L5-ED-01 | HW Valve | FCU-L5-ED-01 | UO7 | FCU | HHWV Actuator
Emergency Department – Main Waiting Room
FCU-L5-ED-02 | [7 empty] | ECB300
Schedule | FCU-L5-ED-02-SW01 | Level 5 | FCU-L5-ED-02 | Schedule | FCU-L5-ED-02 | SW01 | Software | Software Point
Fan Enable | FCU-L5-ED-02-UO1 | Level 5 | FCU-L5-ED-02 | Fan Enable | FCU-L5-ED-02 | UO1 | MSSB | 12VDC Relay
Fan Status | FCU-L5-ED-02-UI1 | Level 5 | FCU-L5-ED-02 | Fan Status | FCU-L5-ED-02 | UI1 | MSSB | CCS
SA Temp | FCU-L5-ED-02-UI2 | Level 5 | FCU-L5-ED-02 | SA Temp | FCU-L5-ED-02 | UI2 | SA Ductwork | PDIGR-TE200BE24B2
Spare | FCU-L5-ED-02-UI3 | Level 5 | FCU-L5-ED-02 | Spare | FCU-L5-ED-02 | UI3 | Space
Dirty Filter | FCU-L5-ED-02-UI4 | Level 5 | FCU-L5-ED-02 | Dirty Filter | FCU-L5-ED-02 | UI4 | Filter Box | AFS - 930.80222524
WZ Space Temp | AHU-L5-ED-1-WZ-UI5 | Level 5 | AHU-L5-ED-1-WZ | WZ Space Temp | AHU-L5-ED-1-WZ | UI5 | Space | PDITE-SENSORX0
Space Temp (Waiting 5003) |  |  | Cat6 Ethernet Cable | RJ45 Connectors both sides | Space Temp |  | Space | EC - Vue Smart Sensor
Spare | FCU-L5-ED-02-UO3 | Level 5 | FCU-L5-ED-02 | Spare | FCU-L5-ED-02 | UO3 | FCU | PDITE-SENSORX0
AH LED WZ-ED-1 | AHU-L5-ED1-WZ-UO4 | Level 5 | AHU-L5-ED1-WZ | AH LED WZ-ED-1 | AHU-L5-ED1-WZ | UO4 | FCU | PDITE-SENSORX0
Spare | FCU-L5-ED-02-UO5 | Level 5 | FCU-L5-ED-02 | Spare | FCU-L5-ED-02 | UO5 | FCU
CHW Valve | FCU-L5-ED-02-UO6 | Level 5 | FCU-L5-ED-02 | CHW Valve | FCU-L5-ED-02 | UO6 | FCU | CHWV Actuator
HW Valve | FCU-L5-ED-02-UO7 | Level 5 | FCU-L5-ED-02 | HW Valve | FCU-L5-ED-02 | UO7 | FCU | HHWV Actuator
Fan Speed | FCU-L5-ED-02-UO8 | Level 5 | FCU-L5-ED-02 | Fan Speed | FCU-L5-ED-02 | UO8 | FCU | Terminals
Radiology – X-ray Rooms
FCU-L5-RD-01 | [7 empty] | ECB400
Schedule | FCU-L5-RD-01-SW01 | Level 5 | FCU-L5-RD-01 | Schedule | FCU-L5-RD-01 | SW01 | Software | Software Point
Fan Enable | FCU-L5-RD-01-UO1 | Level 5 | FCU-L5-RD-01 | Fan Enable | FCU-L5-RD-01 | UO1 | MSSB | 12VDC Relay
Fan Status | FCU-L5-RD-01-UI1 | Level 5 | FCU-L5-RD-01 | Fan Status | FCU-L5-RD-01 | UI1 | MSSB | AFS - 930.80222524
SA Temp | FCU-L5-RD-01-UI2 | Level 5 | FCU-L5-RD-01 | SA Temp | FCU-L5-RD-01 | UI2 | SA Ductwork | PDIGR-TE200BE24B2
Spare | FCU-L5-RD-01-UI3 | Level 5 | FCU-L5-RD-01 | Spare | FCU-L5-RD-01 | UI3 | Space
Space Temp 2 | FCU-L5-RD-01-UI4 | Level 5 | FCU-L5-RD-01 | Space Temp 2 | FCU-L5-RD-01 | UI4 | Space | PDITE-SENSORX0
Space Temp 3 | FCU-L5-RD-01-UI5 | Level 5 | FCU-L5-RD-01 | Space Temp 3 | FCU-L5-RD-01 | UI5 | Filter Box | PDITE-SENSORX0
Dirty Filter | FCU-L5-RD-01-UI6 | Level 5 | FCU-L5-RD-01 | Dirty Filter | FCU-L5-RD-01 | UI6 | Filter Box | AFS - 930.80222524
Small Drug Fridge Temp (Rm 5198 Clean Utility) | Fridges-UI7 | Level 5 | Fridges | Small Drug Fridge Temp (Rm 5198 Clean Utility) | Fridges | UI7 | Space | PDIGR-TE200BE24B2
Small Drug Fridge Fault (Rm 5198 Clean Utility) | Fridges-UI8 | Level 5 | Fridges | Small Drug Fridge Fault (Rm 5198 Clean Utility) | Fridges | UI8 | Space | Terminals
Space Temp 1 |  |  | Cat6 Ethernet Cable | RJ45 Connectors both sides | Space Temp |  | Space | EC - Vue Smart Sensor
Zone 1 SSR Heating (Gen X-Ray 5403) | FCU-L5-RD-01-UO2 | Level 5 | FCU-L5-RD-01 | Zone 1 SSR Heating (Gen X-Ray 5403) | FCU-L5-RD-01 | UO2 | FCU | SSR Module
Zone 2 SSR Heating (Gen X-Ray 5404) | FCU-L5-RD-01-UO3 | Level 5 | FCU-L5-RD-01 | Zone 2 SSR Heating (Gen X-Ray 5404) | FCU-L5-RD-01 | UO3 | FCU | SSR Module
CHW Valve | FCU-L5-RD-01-UO4 | Level 5 | FCU-L5-RD-01 | CHW Valve | FCU-L5-RD-01 | UO4 | FCU | CHWV Actuator
HW Valve | FCU-L5-RD-01-UO5 | Level 5 | FCU-L5-RD-01 | HW Valve | FCU-L5-RD-01 | UO5 | FCU | HHWV Actuator
Spare | FCU-L5-RD-01-UO6 | Level 5 | FCU-L5-RD-01 | Spare | FCU-L5-RD-01 | UO6 | FCU
AH LED 2 | FCU-L5-RD-01-UO7 | Level 5 | FCU-L5-RD-01 | AH LED 2 | FCU-L5-RD-01 | UO7 | FCU | PDITE-SENSORX0
AH LED 3 | FCU-L5-RD-01-UO8 | Level 5 | FCU-L5-RD-01 | AH LED 3 | FCU-L5-RD-01 | UO8 | FCU | PDITE-SENSORX0
Radiology – CT Scanning Rooms
FCU-L5-RD-02 | [7 empty] | ECB600
Schedule | FCU-L5-RD-02-SW01 | Level 5 | FCU-L5-RD-02 | Schedule | FCU-L5-RD-02 | SW01 | Software | Software Point
Fan Enable | FCU-L5-RD-02-UO1 | Level 5 | FCU-L5-RD-02 | Fan Enable | FCU-L5-RD-02 | UO1 | MSSB | 12VDC Relay
Fan Status | FCU-L5-RD-02-UI1 | Level 5 | FCU-L5-RD-02 | Fan Status | FCU-L5-RD-02 | UI1 | MSSB | AFS - 930.80222524
SA Temp | FCU-L5-RD-02-UI2 | Level 5 | FCU-L5-RD-02 | SA Temp | FCU-L5-RD-02 | UI2 | SA Ductwork | PDIGR-TE200BE24B2
Spare | FCU-L5-RD-02-UI3 | Level 5 | FCU-L5-RD-02 | Spare | FCU-L5-RD-02 | UI3 | Space
Space Temp 2 | FCU-L5-RD-02-UI4 | Level 5 | FCU-L5-RD-02 | Space Temp 2 | FCU-L5-RD-02 | UI4 | Space | PDITE-SENSORX0
Dirty Filter | FCU-L5-RD-02-UI5 | Level 5 | FCU-L5-RD-02 | Dirty Filter | FCU-L5-RD-02 | UI5 | Filter Box | AFS - 930.80222524
CZ Space Temp | AHU-L5-ED2-CZ-UI6 | Level 5 | AHU-L5-ED2-CZ | CZ Space Temp | AHU-L5-ED2-CZ | UI6 | Space | PDITE-SENSORX0
SZ Space Temp | AHU-L5-ED2-SZ-UI7 | Level 5 | AHU-L5-ED2-SZ | SZ Space Temp | AHU-L5-ED2-SZ | UI7 | Space | PDITE-SENSORX0
CZ Space Temp | AHU-L5-ED1-CZ-UI8 | Level 5 | AHU-L5-ED1-CZ | CZ Space Temp | AHU-L5-ED1-CZ | UI8 | Space | PDITE-SENSORX0
Small Drug Fridge Temp (Rm5157 Drug Store) | Fridges-UI9 | Level 5 | Fridges | Small Drug Fridge Temp (Rm5157 Drug Store) | Fridges | UI9 | Space | PDIGR-TE200BE24B2
Small Drug Fridge Fault (Rm5157 Drug Store) | Fridges-UI10 | Level 5 | Fridges | Small Drug Fridge Fault (Rm5157 Drug Store) | Fridges | UI10 | Space | Terminals
Space Temp 1 |  |  | Cat6 Ethernet Cable | RJ45 Connectors both sides | Space Temp |  | Space | EC - Vue Smart Sensor
Zone 1 SSR Heating (Scanning 5400) | FCU-L5-RD-02-UO2 | Level 5 | FCU-L5-RD-02 | Zone 1 SSR Heating (Scanning 5400) | FCU-L5-RD-02 | UO2 | FCU | SSR Module
Zone 2 SSR Heating (CT Control 5401) | FCU-L5-RD-02-UO3 | Level 5 | FCU-L5-RD-02 | Zone 2 SSR Heating (CT Control 5401) | FCU-L5-RD-02 | UO3 | FCU | SSR Module
CHW Valve | FCU-L5-RD-02-UO4 | Level 5 | FCU-L5-RD-02 | CHW Valve | FCU-L5-RD-02 | UO4 | FCU | CHWV Actuator
HW Valve | FCU-L5-RD-02-UO5 | Level 5 | FCU-L5-RD-02 | HW Valve | FCU-L5-RD-02 | UO5 | FCU | HHWV Actuator
Fan Speed | FCU-L5-ED-02-UO6 | Level 5 | FCU-L5-ED-02 | Fan Speed | FCU-L5-ED-02 | UO6 | FCU | Terminals
Spare | FCU-L5-ED-02-UO7 | Level 5 | FCU-L5-ED-02 | Spare | FCU-L5-ED-02 | UO7 | FCU
AH LED 2 | FCU-L5-ED-02-UO8 | Level 5 | FCU-L5-ED-02 | AH LED 2 | FCU-L5-ED-02 | UO8 | FCU | PDITE-SENSORX0
AH LED CZ-ED-2 |  |  | AHU-L5-ED-2-CZ | AH LED CZ-ED-2 | AHU-L5-ED-2-CZ | UO9 | FCU | PDITE-SENSORX0
AH LED SZ-ED-2 |  |  | AHU-L5-ED-2-CZ | AH LED SZ-ED-2 | AHU-L5-ED-2-CZ | UO10 | FCU | PDITE-SENSORX0
AH LED CZ-ED-1 |  |  | AHU-L5-ED-1-CZ | AH LED CZ-ED-1 | AHU-L5-ED-1-CZ | UO11 | FCU | PDITE-SENSORX0
Level 6
Level 6 - Temporary AC
FCU-L6-01 | [7 empty] | ECB203
Schedule | FCU-L6-01-SW01 | Level-6 | FCU-L6-01 | Schedule | FCU-L6-01 | SW01 | Software | Software Point
Fan Enable | FCU-L6-01-DO1 | Level-6 | FCU-L6-01 | Fan Enable | FCU-L6-01 | DO1 | MSSB | 24VAC Relay
Fan Status | FCU-L6-01-UI1 | Level-6 | FCU-L6-01 | Fan Status | FCU-L6-01 | UI1 | MSSB | CCS
SA Temp | FCU-L6-01-UI2 | Level-6 | FCU-L6-01 | SA Temp | FCU-L6-01 | UI2 | SA Ductwork | PDIGR-TE200BE24B2
Space Temp | FCU-L6-01-UI3 | Level-6 | FCU-L6-01 | Space Temp | FCU-L6-01 | UI3 | RA Ductwork | PDITE-SENSORX0
Dirty Filter | FCU-L6-01-UI4 | Level-6 | FCU-L6-01 | Dirty Filter | FCU-L6-01 | UI4 | Filter Box | AFS - 930.80222524
Fire | L6 Fire-UI5 | Level-6 | FCU-L6-01 | Fire | L6 Fire | UI5 | MSSB | 24VAC Relay
CHW Valve | FCU-L6-01-UO6 | Level-6 | FCU-L6-01 | CHW Valve | FCU-L6-01 | UO6 | FCU | CHWV Actuator
HW Valve | FCU-L6-01-UO7 | Level-6 | FCU-L6-01 | HW Valve | FCU-L6-01 | UO7 | FCU | HHWV Actuator
Fan Speed | FCU-L6-01-UO8 | Level 5 | FCU-L6-01 | Fan Speed | FCU-L6-01 | UO8 | FCU | Terminals
Level 7
Comms Rooms
FCU-L7-01 | [7 empty] | ECB203
Schedule | FCU-L7-01-SW01 | Level-7 | FCU-L7-01 | Schedule | FCU-L7-01 | SW01 | Software | Software Point
Fan Enable | FCU-L7-01-DO1 | Level-7 | FCU-L7-01 | Fan Enable | FCU-L7-01 | DO1 | MSSB | 24VAC Relay
Fan Status | FCU-L7-01-UI1 | Level-7 | FCU-L7-01 | Fan Status | FCU-L7-01 | UI1 | MSSB | CCS
SA Temp | FCU-L7-01-UI2 | Level-7 | FCU-L7-01 | SA Temp | FCU-L7-01 | UI2 | SA Ductwork | PDIGR-TE200BE24B2
Space Temp | FCU-L7-01-UI3 | Level-7 | FCU-L7-01 | Space Temp | FCU-L7-01 | UI3 | Space | PDITE-SENSORX0
Dirty Filter | FCU-L7-01-UI4 | Level-7 | FCU-L7-01 | Dirty Filter | FCU-L7-01 | UI4 | Filter Box | AFS - 930.80222524
CHW Valve | FCU-L7-01-UO6 | Level-7 | FCU-L7-01 | CHW Valve | FCU-L7-01 | UO6 | FCU | CHWV Actuator
Lift Lobby and Corridor Areas
FCU-L7-02 | [7 empty] | ECB203
Schedule | FCU-L7-02-SW01 | Level-7 | FCU-L7-02 | Schedule | FCU-L7-02 | SW01 | Software | Software Point
Fan Enable | FCU-L7-02-DO1 | Level-7 | FCU-L7-02 | Fan Enable | FCU-L7-02 | DO1 | MSSB | 24VAC Relay
Fan Status | FCU-L7-02-UI1 | Level-7 | FCU-L7-02 | Fan Status | FCU-L7-02 | UI1 | MSSB | CCS
SA Temp | FCU-L7-02-UI2 | Level-7 | FCU-L7-02 | SA Temp | FCU-L7-02 | UI2 | SA Ductwork | PDIGR-TE200BE24B2
RA Temp | FCU-L7-02-UI3 | Level-7 | FCU-L7-02 | RA Temp | FCU-L7-02 | UI3 | RA Ductwork | PDIGR-TE200BE24B2
Dirty Filter | FCU-L7-02-UI4 | Level-7 | FCU-L7-02 | Dirty Filter | FCU-L7-02 | UI4 | Filter Box | AFS - 930.80222524
CHW Valve | FCU-L7-02-UO6 | Level-7 | FCU-L7-02 | CHW Valve | FCU-L7-02 | UO6 | FCU | CHWV Actuator
HW Valve | FCU-L7-02-UO7 | Level-7 | FCU-L7-02 | HW Valve | FCU-L7-02 | UO7 | FCU | HHWV Actuator
Lift Lobby and Corridor Areas
FCU-L7-03 | [7 empty] | ECB203
Schedule | FCU-L7-03-SW01 | Level-7 | FCU-L7-03 | Schedule | FCU-L7-03 | SW01 | Software | Software Point
Fan Enable | FCU-L7-03-DO1 | Level-7 | FCU-L7-03 | Fan Enable | FCU-L7-03 | DO1 | MSSB | 24VAC Relay
Fan Status | FCU-L7-03-UI1 | Level-7 | FCU-L7-03 | Fan Status | FCU-L7-03 | UI1 | MSSB | CCS
SA Temp | FCU-L7-03-UI2 | Level-7 | FCU-L7-03 | SA Temp | FCU-L7-03 | UI2 | SA Ductwork | PDIGR-TE200BE24B2
RA Temp | FCU-L7-03-UI3 | Level-7 | FCU-L7-03 | RA Temp | FCU-L7-03 | UI3 | RA Ductwork | PDIGR-TE200BE24B2
Dirty Filter | FCU-L7-03-UI4 | Level-7 | FCU-L7-03 | Dirty Filter | FCU-L7-03 | UI4 | Filter Box | AFS - 930.80222524
CHW Valve | FCU-L7-03-UO6 | Level-7 | FCU-L7-03 | CHW Valve | FCU-L7-03 | UO6 | FCU | CHWV Actuator
HW Valve | FCU-L7-03-UO7 | Level-7 | FCU-L7-03 | HW Valve | FCU-L7-03 | UO7 | FCU | HHWV Actuator
IMT/Maintenance Work Room
FCU-L7-04 | [7 empty] | ECB203
Schedule | FCU-L7-04-SW01 | Level-7 | FCU-L7-04 | Schedule | FCU-L7-04 | SW01 | Software | Software Point
Fan Enable | FCU-L7-04-DO1 | Level-7 | FCU-L7-04 | Fan Enable | FCU-L7-04 | DO1 | MSSB | 24VAC Relay
Fan Status | FCU-L7-04-UI1 | Level-7 | FCU-L7-04 | Fan Status | FCU-L7-04 | UI1 | MSSB | CCS
SA Temp | FCU-L7-04-UI2 | Level-7 | FCU-L7-04 | SA Temp | FCU-L7-04 | UI2 | SA Ductwork | PDIGR-TE200BE24B2
Spare | FCU-L7-04-UI3 | Level-7 | FCU-L7-04 | Spare | FCU-L7-04 | UI3 | Space
Dirty Filter | FCU-L7-04-UI4 | Level-7 | FCU-L7-04 | Dirty Filter | FCU-L7-04 | UI4 | Filter Box | AFS - 930.80222524
Space Temp (Maintenance Rm) |  |  | Cat6 Ethernet Cable | RJ45 Connectors both sides | Space Temp |  | Space | EC - Vue Smart Sensor
CHW Valve | FCU-L7-04-UO6 | Level-7 | FCU-L7-04 | CHW Valve | FCU-L7-04 | UO6 | FCU | CHWV Actuator
HW Valve | FCU-L7-04-UO7 | Level-7 | FCU-L7-04 | HW Valve | FCU-L7-04 | UO7 | FCU | HHWV Actuator
MISC-L7-1 |  |  |  | L7 WEST BMS Panel |  |  |  | ECB600
EF-L5-02/03 Fan Status | MISC-L7-1-UI1 | Level-7 | Iso Room | EF-L5-02/03 Fan Status | MISC-L7-1 | UI1 | EA Duct ISO 1 | AFS - 930.80222524
EF-L5-04/05 Fan Status | MISC-L7-1-UI2 | Level-7 | Iso Room | EF-L5-04/05 Fan Status | MISC-L7-1 | UI2 | EA Duct ISO 2 | AFS - 930.80222524
CRAC-L7-1 Space Temp | MISC-L7-1-UI3 | Level-7 | Server Room | CRAC-L7-1 Space Temp | MISC-L7-1 | UI3 | Space | QFM2160 Temp
CRAC-L7-1 Space RH | MISC-L7-1-UI4 | Level-7 | Server Room | CRAC-L7-1 Space RH | MISC-L7-1 | UI4 | Space | QFM2160 Humidity
CRAC-L7-2 Space Temp | MISC-L7-1-UI5 | Level-7 | Server Room | CRAC-L7-2 Space Temp | MISC-L7-1 | UI5 | Space | QFM2160 Temp
CRAC-L7-2 Space RH | MISC-L7-1-UI6 | Level-7 | Server Room | CRAC-L7-2 Space RH | MISC-L7-1 | UI6 | Space | QFM2160 Humidity
CRAC-L7-1 Wet Switch | MISC-L7-1-UI7 | Level-7 | Server Room | CRAC-L7-1 Wet Switch | MISC-L7-1 | UI7 | Safety Tray | PT-015 (WS)
CRAC-L7-2 Wet Switch | MISC-L7-1-UI8 | Level-7 | Server Room | CRAC-L7-2 Wet Switch | MISC-L7-1 | UI8 | Safety Tray | PT-015 (WS)
VESDA GAS Alarm #1 | MISC-L7-1-UI9 | Level-7 | Server Room | VESDA GAS Alarm #1 | MISC-L7-1 | UI9 | Alarm Panel | Terminals
VESDA GAS Alarm #2 | MISC-L7-1-UI10 | Level-7 | Server Room | VESDA GAS Alarm #2 | MISC-L7-1 | UI10 | Alarm Panel | Terminals
VESDA GAS Alarm #3 | MISC-L7-1-UI11 | Level-7 | Server Room | VESDA GAS Alarm #3 | MISC-L7-1 | UI11 | Alarm Panel | Terminals
VESDA GAS Alarm #4 | MISC-L7-1-UI12 | Level-7 | Server Room | VESDA GAS Alarm #4 | MISC-L7-1 | UI12 | Alarm Panel | Terminals
Nurse Call System General Alarm | MISC-L7-2-UI13 | Nurse Call System | Nurse Call Panel | Nurse Call System General Alarm | MISC-L7-2 | UI13 | Nurse Call Panel | Terminals
Nurse Call System Fault | MISC-L7-2-UI14 | Nurse Call System | Nurse Call Panel | Nurse Call System Fault | MISC-L7-2 | UI14 | Nurse Call Panel | Terminals
Fire | MISC-L7-1-UI15 | Level-7 | Fire | Fire | MISC-L7-1 | UI15 | MSSB | Terminals
EF-L5-02/03 EA Damper | MISC-L7-1-UO1 | Level-7 | Iso Room | EF-L5-02/03 EA Damper | MISC-L7-1 | UO1 | EA Duct ISO 1 | GDB161.1E
EF-L5-04/05 EA Damper | MISC-L7-1-UO2 | Level-7 | Iso Room | EF-L5-04/05 EA Damper | MISC-L7-1 | UO2 | EA Duct ISO 1 | GDB161.1E
OAF-L7-01 Fan Enable | MISC-L7-1-UO3 | Level-7 | Fans | OAF-L7-01 Fan Enable | MISC-L7-1 | UO3 | MSSB | 12VDC Relay
OAF-L7-02 Fan Enable | MISC-L7-1-UO4 | Level-7 | Fans | OAF-L7-02 Fan Enable | MISC-L7-1 | UO4 | MSSB | 12VDC Relay
OAF-L7-03 Fan Enable | MISC-L7-1-UO5 | Level-7 | Fans | OAF-L7-03 Fan Enable | MISC-L7-1 | UO5 | MSSB | 12VDC Relay
MISC-L7-2 |  |  |  | L7 EAST BMS Panel |  |  |  | ECB600
Gas Alarm Panel Fault | MISC-L7-2-UI1 | Med Gas | Med Gas | Gas Alarm Panel Fault | MISC-L7-2 | UI1 | Med Gas | Terminals
Vacuum Pump 1 Status | MISC-L7-2-UI2 | Vacuum Pump | Vacuum Pump | Vacuum Pump 1 Status | MISC-L7-2 | UI2 | Vacuum Pump | Terminals
Vacuum Pump 2 Status | MISC-L7-2-UI3 | Vacuum Pump | Vacuum Pump | Vacuum Pump 2 Status | MISC-L7-2 | UI3 | Vacuum Pump | Terminals
Compressor Status | MISC-L7-2-UI4 | Compressed Air | Compressed Air | Compressor Status | MISC-L7-2 | UI4 | Compressed Air | Terminals
Fire Alarm | MISC-L7-2-UI5 | Fire | Fire | Fire Alarm | MISC-L7-2 | UI5 | Fire | Terminals
Fire Panel Fault x | MISC-L7-2-UI6 | Fire | Fire | Fire Panel Fault x | MISC-L7-2 | UI6 | Fire | Terminals
EWIS Alarm | MISC-L7-2-UI7 | Fire | Fire | EWIS Alarm | MISC-L7-2 | UI7 | Fire | Terminals
EWIS Fault | MISC-L7-2-UI8 | Fire | Fire | EWIS Fault | MISC-L7-2 | UI8 | Fire | Terminals
Lifts Status | MISC-L7-2-UI9 | Lifts | Lifts | Lifts Status | MISC-L7-2 | UI9 | Lifts | Lift Terminals
Lifts Fault | MISC-L7-2-UI10 | Lifts | Lifts | Lifts Fault | MISC-L7-2 | UI10 | Lifts | Lift Terminals
OAF-L7-01 Status | MISC-L7-1-UI11 | Level-7 | Fans | OAF-L7-01 Status | MISC-L7-1 | UI11 | MSSB | CCS
OAF-L7-02 Status | MISC-L7-1-UI12 | Level-7 | Fans | OAF-L7-02 Status | MISC-L7-1 | UI12 | MSSB | CCS
OAF-L7-03 Status | MISC-L7-1-UI13 | Level-7 | Fans | OAF-L7-03 Status | MISC-L7-1 | UI13 | MSSB | CCS
Vacuum Pump 1 Start/Stop | MISC-L7-2-UO1 | Vacuum Pump | Vacuum Pump | Vacuum Pump 1 Start/Stop | MISC-L7-2 | UO1 | Vacuum Pump | 12VDC Relay
Vacuum Pump 2 Start/Stop | MISC-L7-2-UO2 | Vacuum Pump | Vacuum Pump | Vacuum Pump 2 Start/Stop | MISC-L7-2 | UO2 | Vacuum Pump | 12VDC Relay
Compressor Start / Stop | MISC-L7-2-UO3 | Compressed Air | Compressed Air | Compressor Start / Stop | MISC-L7-2 | UO3 | Compressed Air | 12VDC Relay
OAF-L7-01 Fan Enable | MISC-L7-1-UO4 | Level-7 | Fans | OAF-L7-01 Fan Enable | MISC-L7-1 | UO4 | MSSB | 12VDC Relay
OAF-L7-02 Fan Enable | MISC-L7-1-UO5 | Level-7 | Fans | OAF-L7-02 Fan Enable | MISC-L7-1 | UO5 | MSSB | 12VDC Relay
OAF-L7-03 Fan Enable | MISC-L7-1-UO6 | Level-7 | Fans | OAF-L7-03 Fan Enable | MISC-L7-1 | UO6 | MSSB | 12VDC Relay
Level 5 Emergency Department Support
AHU-L5-ED1 | [7 empty] | ECB600
Schedule | AHU-L5-ED1-SW01 | Level-7 | AHU-L5-ED1 | Schedule | AHU-L5-ED1 | SW01 | Software | Software Point
CHW Offcoil Temp | AHU-L5-ED1-UI1 | Level-7 | AHU-L5-ED1 | CHW Offcoil Temp | AHU-L5-ED1 | UI1 | Plenum Offcoil | PDIGR-TE200FDB24A
RA Temp | AHU-L5-ED1-UI2 | Level-7 | AHU-L5-ED1 | RA Temp | AHU-L5-ED1 | UI2 | RA Ductwork | QFM2160 Temp
RA Humidity | AHU-L5-ED1-UI3 | Level-7 | AHU-L5-ED1 | RA Humidity | AHU-L5-ED1 | UI3 | RA Ductwork | QFM2160 Humidity
Dirty Filter | AHU-L5-ED1-UI4 | Level-7 | AHU-L5-ED1 | Dirty Filter | AHU-L5-ED1 | UI4 | Filter Box | AFS - 930.80222524
NZ SA Temp | AHU-L5-ED1-UI5 | Level-7 | AHU-L5-ED1 | NZ SA Temp | AHU-L5-ED1 | UI5 | Zone SA Ductwork | PDIGR-TE200BE24B2
SZ SA Temp | AHU-L5-ED1-UI6 | Level-7 | AHU-L5-ED1 | SZ SA Temp | AHU-L5-ED1 | UI6 | Zone SA Ductwork | PDIGR-TE200BE24B2
WZ SA Temp | AHU-L5-ED1-UI7 | Level-7 | AHU-L5-ED1 | WZ SA Temp | AHU-L5-ED1 | UI7 | Zone SA Ductwork | PDIGR-TE200BE24B2
CZ SA Temp | AHU-L5-ED1-UI8 | Level-7 | AHU-L5-ED1 | CZ SA Temp | AHU-L5-ED1 | UI8 | Zone SA Ductwork | PDIGR-TE200BE24B2
CHW Valve | AHU-L5-ED1-UO1 | Level-7 | AHU-L5-ED1 | CHW Valve | AHU-L5-ED1 | UO1 | AHU | CHWV Actuator
OA Damper | AHU-L5-ED1-UO2 | Level-7 | AHU-L5-ED1 | OA Damper | AHU-L5-ED1 | UO2 | AHU | GDB161.1E
EA Damper | AHU-L5-ED1-UO3 | Level-7 | AHU-L5-ED1 | EA Damper | AHU-L5-ED1 | UO3 | AHU | GDB161.1E
RA Damper | AHU-L5-ED1-UO4 | Level-7 | AHU-L5-ED1 | RA Damper | AHU-L5-ED1 | UO4 | AHU | GDB161.1E
NZ F&B Actuator | AHU-L5-ED1-UO5 | Level-7 | AHU-L5-ED1 | NZ F&B Actuator | AHU-L5-ED1 | UO5 | AHU | GDB161.1E
SZ F&B Actuator | AHU-L5-ED1-UO6 | Level-7 | AHU-L5-ED1 | SZ F&B Actuator | AHU-L5-ED1 | UO6 | AHU | GDB161.1E
WZ F&B Actuator | AHU-L5-ED1-UO7 | Level-7 | AHU-L5-ED1 | WZ F&B Actuator | AHU-L5-ED1 | UO7 | AHU | GDB161.1E
CZ F&B Actuator | AHU-L5-ED1-UO8 | Level-7 | AHU-L5-ED1 | CZ F&B Actuator | AHU-L5-ED1 | UO8 | AHU | GDB161.1E
NZ HW Valve | AHU-L5-ED1-UO9 | Level-7 | AHU-L5-ED1 | NZ HW Valve | AHU-L5-ED1 | UO9 | AHU | HHWV Actuator
SZ HW Valve | AHU-L5-ED1-UO10 | Level-7 | AHU-L5-ED1 | SZ HW Valve | AHU-L5-ED1 | UO10 | AHU | HHWV Actuator
WZ HW Valve | AHU-L5-ED1-UO11 | Level-7 | AHU-L5-ED1 | WZ HW Valve | AHU-L5-ED1 | UO11 | AHU | HHWV Actuator
CZ HW Valve | AHU-L5-ED1-UO12 | Level-7 | AHU-L5-ED1 | CZ HW Valve | AHU-L5-ED1 | UO12 | AHU | HHWV Actuator
Level 5 Emergency Department
AHU-L5-ED2 | [7 empty] | ECB600
Schedule | AHU-L5-ED2-SW01 | Level-7 | AHU-L5-ED2 | Schedule | AHU-L5-ED2 | SW01 | Software | Software Point
CHW Offcoil Temp | AHU-L5-ED2-UI1 | Level-7 | AHU-L5-ED2 | CHW Offcoil Temp | AHU-L5-ED2 | UI1 | Plenum Offcoil | PDIGR-TE200FDB24A
RA Temp | AHU-L5-ED2-UI2 | Level-7 | AHU-L5-ED2 | RA Temp | AHU-L5-ED2 | UI2 | RA Ductwork | QFM2160 Temp
RA Humidity | AHU-L5-ED2-UI3 | Level-7 | AHU-L5-ED2 | RA Humidity | AHU-L5-ED2 | UI3 | RA Ductwork | QFM2160 Humidity
Dirty Filter | AHU-L5-ED2-UI4 | Level-7 | AHU-L5-ED2 | Dirty Filter | AHU-L5-ED2 | UI4 | Filter Box | AFS - 930.80222524
NZ SA Temp | AHU-L5-ED2-UI5 | Level-7 | AHU-L5-ED2 | NZ SA Temp | AHU-L5-ED2 | UI5 | Zone SA Ductwork | PDIGR-TE200BE24B2
SZ SA Temp | AHU-L5-ED2-UI6 | Level-7 | AHU-L5-ED2 | SZ SA Temp | AHU-L5-ED2 | UI6 | Zone SA Ductwork | PDIGR-TE200BE24B2
EZ SA Temp | AHU-L5-ED2-UI7 | Level-7 | AHU-L5-ED2 | EZ SA Temp | AHU-L5-ED2 | UI7 | Zone SA Ductwork | PDIGR-TE200BE24B2
CZ SA Temp | AHU-L5-ED2-UI8 | Level-7 | AHU-L5-ED2 | CZ SA Temp | AHU-L5-ED2 | UI8 | Zone SA Ductwork | PDIGR-TE200BE24B2
CHW Valve | AHU-L5-ED2-UO1 | Level-7 | AHU-L5-ED2 | CHW Valve | AHU-L5-ED2 | UO1 | AHU | CHWV Actuator
OA Damper | AHU-L5-ED2-UO2 | Level-7 | AHU-L5-ED2 | OA Damper | AHU-L5-ED2 | UO2 | AHU | GDB161.1E
EA Damper | AHU-L5-ED2-UO3 | Level-7 | AHU-L5-ED2 | EA Damper | AHU-L5-ED2 | UO3 | AHU | GDB161.1E
RA Damper | AHU-L5-ED2-UO4 | Level-7 | AHU-L5-ED2 | RA Damper | AHU-L5-ED2 | UO4 | AHU | GDB161.1E
NZ F&B Actuator | AHU-L5-ED2-UO5 | Level-7 | AHU-L5-ED2 | NZ F&B Actuator | AHU-L5-ED2 | UO5 | AHU | GDB161.1E
SZ F&B Actuator | AHU-L5-ED2-UO6 | Level-7 | AHU-L5-ED2 | SZ F&B Actuator | AHU-L5-ED2 | UO6 | AHU | GDB161.1E
EZ F&B Actuator | AHU-L5-ED2-UO7 | Level-7 | AHU-L5-ED2 | EZ F&B Actuator | AHU-L5-ED2 | UO7 | AHU | GDB161.1E
CZ F&B Actuator | AHU-L5-ED2-UO8 | Level-7 | AHU-L5-ED2 | CZ F&B Actuator | AHU-L5-ED2 | UO8 | AHU | GDB161.1E
NZ HW Valve | AHU-L5-ED2-UO9 | Level-7 | AHU-L5-ED2 | NZ HW Valve | AHU-L5-ED2 | UO9 | AHU | HHWV Actuator
SZ HW Valve | AHU-L5-ED2-UO10 | Level-7 | AHU-L5-ED2 | SZ HW Valve | AHU-L5-ED2 | UO10 | AHU | HHWV Actuator
EZ HW Valve | AHU-L5-ED2-UO11 | Level-7 | AHU-L5-ED2 | EZ HW Valve | AHU-L5-ED2 | UO11 | AHU | HHWV Actuator
CZ HW Valve | AHU-L5-ED2-UO12 | Level-7 | AHU-L5-ED2 | CZ HW Valve | AHU-L5-ED2 | UO12 | AHU | HHWV Actuator
SAF-L5-ED1 | [7 empty] | VSD-SAF-L5-ED1
Enable | SAF-L5-ED1-SW01 | Level-7 | SAF-L5-ED1 | Enable | SAF-L5-ED1 | SW01 | Level-7 | -
Status | SAF-L5-ED1-SW02 | Level-7 | SAF-L5-ED1 | Status | SAF-L5-ED1 | SW02 | Level-7 | -
VSD Fault | SAF-L5-ED1-SW03 | Level-7 | SAF-L5-ED1 | VSD Fault | SAF-L5-ED1 | SW03 | Level-7 | -
VSD Speed Control | SAF-L5-ED1-SW04 | Level-7 | SAF-L5-ED1 | VSD Speed Control | SAF-L5-ED1 | SW04 | Level-7 | -
RAF-L5-ED1 | [7 empty] | VSD-RAF-L5-ED1
Enable | RAF-L5-ED1-SW01 | Level-7 | RAF-L5-ED1 | Enable | RAF-L5-ED1 | SW01 | Level-7 | -
Status | RAF-L5-ED1-SW02 | Level-7 | RAF-L5-ED1 | Status | RAF-L5-ED1 | SW02 | Level-7 | -
VSD Fault | RAF-L5-ED1-SW03 | Level-7 | RAF-L5-ED1 | VSD Fault | RAF-L5-ED1 | SW03 | Level-7 | -
VSD Speed Control | RAF-L5-ED1-SW04 | Level-7 | RAF-L5-ED1 | VSD Speed Control | RAF-L5-ED1 | SW04 | Level-7 | -
SAF-L5-ED2 | [7 empty] | VSD-SAF-L5-ED2
Enable | SAF-L5-ED2-SW01 | Level-7 | SAF-L5-ED2 | Enable | SAF-L5-ED2 | SW01 | Level-7 | -
Status | SAF-L5-ED2-SW02 | Level-7 | SAF-L5-ED2 | Status | SAF-L5-ED2 | SW02 | Level-7 | -
VSD Fault | SAF-L5-ED2-SW03 | Level-7 | SAF-L5-ED2 | VSD Fault | SAF-L5-ED2 | SW03 | Level-7 | -
VSD Speed Control | SAF-L5-ED2-SW04 | Level-7 | SAF-L5-ED2 | VSD Speed Control | SAF-L5-ED2 | SW04 | Level-7 | -
RAF-L5-ED2 | [7 empty] | VSD-RAF-L5-ED2
Enable | RAF-L5-ED2-SW01 | Level-7 | RAF-L5-ED2 | Enable | RAF-L5-ED2 | SW01 | Level-7 | -
Status | RAF-L5-ED2-SW02 | Level-7 | RAF-L5-ED2 | Status | RAF-L5-ED2 | SW02 | Level-7 | -
VSD Fault | RAF-L5-ED2-SW03 | Level-7 | RAF-L5-ED2 | VSD Fault | RAF-L5-ED2 | SW03 | Level-7 | -
VSD Speed Control | RAF-L5-ED2-SW04 | Level-7 | RAF-L5-ED2 | VSD Speed Control | RAF-L5-ED2 | SW04 | Level-7 | -
Level 4 Renal Department
AHU-L4-RN | [7 empty] | ECB600
Schedule | AHU-L4-RN-SW01 | Level-7 | AHU-L4-RN | Schedule | AHU-L4-RN | SW01 | Software | Software Point
CHW Offcoil Temp | AHU-L4-RN-UI1 | Level-7 | AHU-L4-RN | CHW Offcoil Temp | AHU-L4-RN | UI1 | Plenum Offcoil | PDIGR-TE200FDB24A
RA Temp | AHU-L4-RN-UI2 | Level-7 | AHU-L4-RN | RA Temp | AHU-L4-RN | UI2 | RA Ductwork | QFM2160 Temp
RA Humidity | AHU-L4-RN-UI3 | Level-7 | AHU-L4-RN | RA Humidity | AHU-L4-RN | UI3 | RA Ductwork | QFM2160 Humidity
Dirty Filter | AHU-L4-RN-UI4 | Level-7 | AHU-L4-RN | Dirty Filter | AHU-L4-RN | UI4 | Filter Box | AFS - 930.80222524
NZ SA Temp | AHU-L4-RN-UI5 | Level-7 | AHU-L4-RN | NZ SA Temp | AHU-L4-RN | UI5 | Zone SA Ductwork | PDIGR-TE200BE24B2
SZ SA Temp | AHU-L4-RN-UI6 | Level-7 | AHU-L4-RN | SZ SA Temp | AHU-L4-RN | UI6 | Zone SA Ductwork | PDIGR-TE200BE24B2
WZ SA Temp | AHU-L4-RN-UI7 | Level-7 | AHU-L4-RN | WZ SA Temp | AHU-L4-RN | UI7 | Zone SA Ductwork | PDIGR-TE200BE24B2
CZ SA Temp | AHU-L4-RN-UI8 | Level-7 | AHU-L4-RN | CZ SA Temp | AHU-L4-RN | UI8 | Zone SA Ductwork | PDIGR-TE200BE24B2
CHW Valve | AHU-L4-RN-UO1 | Level-7 | AHU-L4-RN | CHW Valve | AHU-L4-RN | UO1 | AHU | CHWV Actuator
OA Damper | AHU-L4-RN-UO2 | Level-7 | AHU-L4-RN | OA Damper | AHU-L4-RN | UO2 | AHU | GDB161.1E
EA Damper | AHU-L4-RN-UO3 | Level-7 | AHU-L4-RN | EA Damper | AHU-L4-RN | UO3 | AHU | GDB161.1E
RA Damper | AHU-L4-RN-UO4 | Level-7 | AHU-L4-RN | RA Damper | AHU-L4-RN | UO4 | AHU | GDB161.1E
NZ F&B Actuator | AHU-L4-RN-UO5 | Level-7 | AHU-L4-RN | NZ F&B Actuator | AHU-L4-RN | UO5 | AHU | GDB161.1E
SZ F&B Actuator | AHU-L4-RN-UO6 | Level-7 | AHU-L4-RN | SZ F&B Actuator | AHU-L4-RN | UO6 | AHU | GDB161.1E
WZ F&B Actuator | AHU-L4-RN-UO7 | Level-7 | AHU-L4-RN | WZ F&B Actuator | AHU-L4-RN | UO7 | AHU | GDB161.1E
CZ F&B Actuator | AHU-L4-RN-UO8 | Level-7 | AHU-L4-RN | CZ F&B Actuator | AHU-L4-RN | UO8 | AHU | GDB161.1E
NZ HW Valve | AHU-L4-RN-UO9 | Level-7 | AHU-L4-RN | NZ HW Valve | AHU-L4-RN | UO9 | AHU | HHWV Actuator
SZ HW Valve | AHU-L4-RN-UO10 | Level-7 | AHU-L4-RN | SZ HW Valve | AHU-L4-RN | UO10 | AHU | HHWV Actuator
WZ HW Valve | AHU-L4-RN-UO11 | Level-7 | AHU-L4-RN | WZ HW Valve | AHU-L4-RN | UO11 | AHU | HHWV Actuator
CZ HW Valve | AHU-L4-RN-UO12 | Level-7 | AHU-L4-RN | CZ HW Valve | AHU-L4-RN | UO12 | AHU | HHWV Actuator
Level 4 Emergency Department
AHU-L4-EDS | [7 empty] | ECB600
CHW Offcoil Temp | AHU-L4-EDS-UI1 | Level-7 | AHU-L4-EDS | CHW Offcoil Temp | AHU-L4-EDS | UI1 | Plenum Offcoil | PDIGR-TE200FDB24A
RA Temp | AHU-L4-EDS-UI2 | Level-7 | AHU-L4-EDS | RA Temp | AHU-L4-EDS | UI2 | RA Ductwork | QFM2160 Temp
RA Humidity | AHU-L4-EDS-UI3 | Level-7 | AHU-L4-EDS | RA Humidity | AHU-L4-EDS | UI3 | RA Ductwork | QFM2160 Humidity
Dirty Filter | AHU-L4-EDS-UI4 | Level-7 | AHU-L4-EDS | Dirty Filter | AHU-L4-EDS | UI4 | Filter Box | AFS - 930.80222524
NZ SA Temp | AHU-L4-EDS-UI5 | Level-7 | AHU-L4-EDS | NZ SA Temp | AHU-L4-EDS | UI5 | Zone SA Ductwork | PDIGR-TE200BE24B2
CZ SA Temp | AHU-L4-EDS-UI6 | Level-7 | AHU-L4-EDS | CZ SA Temp | AHU-L4-EDS | UI6 | Zone SA Ductwork | PDIGR-TE200BE24B2
Ambient Temperature | Ambient Temperature-UI7 | Level-7 | Ambient Temperature | Ambient Temperature | Ambient Temperature | UI7 | Level-7 | QFM2160 Temp
Ambient Humidity | Ambient Humidity-UI8 | Level-7 | Ambient Humidity | Ambient Humidity | Ambient Humidity | UI8 | Level-7 | QFM2160 Humidity
CHW Valve | AHU-L4-EDS-UO1 | Level-7 | AHU-L4-EDS | CHW Valve | AHU-L4-EDS | UO1 | AHU | CHWV Actuator
OA Damper | AHU-L4-EDS-UO2 | Level-7 | AHU-L4-EDS | OA Damper | AHU-L4-EDS | UO2 | AHU | GDB161.1E
EA Damper | AHU-L4-EDS-UO3 | Level-7 | AHU-L4-EDS | EA Damper | AHU-L4-EDS | UO3 | AHU | GDB161.1E
RA Damper | AHU-L4-EDS-UO4 | Level-7 | AHU-L4-EDS | RA Damper | AHU-L4-EDS | UO4 | AHU | GDB161.1E
NZ F&B Actuator | AHU-L4-EDS-UO5 | Level-7 | AHU-L4-EDS | NZ F&B Actuator | AHU-L4-EDS | UO5 | AHU | GDB161.1E
CZ F&B Actuator | AHU-L4-EDS-UO6 | Level-7 | AHU-L4-EDS | CZ F&B Actuator | AHU-L4-EDS | UO6 | AHU | GDB161.1E
NZ HW Valve | AHU-L4-EDS-UO9 | Level-7 | AHU-L4-EDS | NZ HW Valve | AHU-L4-EDS | UO9 | AHU | HHWV Actuator
CZ HW Valve | AHU-L4-EDS-UO10 | Level-7 | AHU-L4-EDS | CZ HW Valve | AHU-L4-EDS | UO10 | AHU | HHWV Actuator
SAF-L4-RN | [7 empty] | VSD-SAF-L4-RN
Enable | SAF-L4-RN-SW01 | Level-7 | SAF-L4-RN | Enable | SAF-L4-RN | SW01 | Level-7 | -
Status | SAF-L4-RN-SW02 | Level-7 | SAF-L4-RN | Status | SAF-L4-RN | SW02 | Level-7 | -
VSD Fault | SAF-L4-RN-SW03 | Level-7 | SAF-L4-RN | VSD Fault | SAF-L4-RN | SW03 | Level-7 | -
VSD Speed Control | SAF-L4-RN-SW04 | Level-7 | SAF-L4-RN | VSD Speed Control | SAF-L4-RN | SW04 | Level-7 | -
RAF-L4-RN | [7 empty] | VSD-RAF-L4-RN
Enable | RAF-L4-RN-SW01 | Level-7 | RAF-L4-RN | Enable | RAF-L4-RN | SW01 | Level-7 | -
Status | RAF-L4-RN-SW02 | Level-7 | RAF-L4-RN | Status | RAF-L4-RN | SW02 | Level-7 | -
VSD Fault | RAF-L4-RN-SW03 | Level-7 | RAF-L4-RN | VSD Fault | RAF-L4-RN | SW03 | Level-7 | -
VSD Speed Control | RAF-L4-RN-SW04 | Level-7 | RAF-L4-RN | VSD Speed Control | RAF-L4-RN | SW04 | Level-7 | -
SAF-L4-EDS | [7 empty] | VSD-SAF-L4-EDS
Enable | SAF-L4-EDS-SW01 | Level-7 | SAF-L4-EDS | Enable | SAF-L4-EDS | SW01 | #REF! | -
Status | SAF-L4-EDS-SW02 | Level-7 | SAF-L4-EDS | Status | SAF-L4-EDS | SW02 | #REF! | -
VSD Fault | SAF-L4-EDS-SW03 | Level-7 | SAF-L4-EDS | VSD Fault | SAF-L4-EDS | SW03 | #REF! | -
VSD Speed Control | SAF-L4-EDS-SW04 | Level-7 | SAF-L4-EDS | VSD Speed Control | SAF-L4-EDS | SW04 | #REF! | -
RAF-L4-EDS | [7 empty] | VSD-RAF-L4-EDS
Enable | RAF-L4-EDS-SW01 | Level-7 | RAF-L4-EDS | Enable | RAF-L4-EDS | SW01 | Level-7 | -
Status | RAF-L4-EDS-SW02 | Level-7 | RAF-L4-EDS | Status | RAF-L4-EDS | SW02 | Level-7 | -
VSD Fault | RAF-L4-EDS-SW03 | Level-7 | RAF-L4-EDS | VSD Fault | RAF-L4-EDS | SW03 | Level-7 | -
VSD Speed Control | RAF-L4-EDS-SW04 | Level-7 | RAF-L4-EDS | VSD Speed Control | RAF-L4-EDS | SW04 | Level-7 | -
Stairs
SPF-01 | [7 empty] | VSD-SPF-01
Enable | SPF-01-SW01 | Level-7 | SPF-01 | Enable | SPF-01 | SW01 | Level-7 | -
Status | SPF-01-SW02 | Level-7 | SPF-01 | Status | SPF-01 | SW02 | Level-7 | -
VSD Fault | SPF-01-SW03 | Level-7 | SPF-01 | VSD Fault | SPF-01 | SW03 | Level-7 | -
VSD Speed Control | SPF-01-SW04 | Level-7 | SPF-01 | VSD Speed Control | SPF-01 | SW04 | Level-7 | -
Static DP transducer |  |  |  | Static DP transducer |  |  |  | QBM2030-1U
Stairs
SPF-02 | [7 empty] | VSD-SPF-02
Enable | SPF-02-SW01 | Level-7 | SPF-02 | Enable | SPF-02 | SW01 | Level-7 | -
Status | SPF-02-SW02 | Level-7 | SPF-02 | Status | SPF-02 | SW02 | Level-7 | -
VSD Fault | SPF-02-SW03 | Level-7 | SPF-02 | VSD Fault | SPF-02 | SW03 | Level-7 | -
VSD Speed Control | SPF-02-SW04 | Level-7 | SPF-02 | VSD Speed Control | SPF-02 | SW04 | Level-7 | -
Static DP transducer |  |  |  | Static DP transducer |  |  |  | QBM2030-1U
GEF-L4-01 | [7 empty] | VSD-GEF-L4-01
Enable | GEF-L4-01-SW01 | Level-7 | GEF-L4-01 | Enable | GEF-L4-01 | SW01 | Level-7 | -
Status | GEF-L4-01-SW02 | Level-7 | GEF-L4-01 | Status | GEF-L4-01 | SW02 | Level-7 | -
VSD Fault | GEF-L4-01-SW03 | Level-7 | GEF-L4-01 | VSD Fault | GEF-L4-01 | SW03 | Level-7 | -
VSD Speed Control | GEF-L4-01-SW04 | Level-7 | GEF-L4-01 | VSD Speed Control | GEF-L4-01 | SW04 | Level-7 | -
Autopsy Room
GEF-L4-02 | [7 empty] | VSD-GEF-L4-02
Enable | GEF-L4-02-SW01 | Level-7 | GEF-L4-02 | Enable | GEF-L4-02 | SW01 | Level-7 | -
Status | GEF-L4-02-SW02 | Level-7 | GEF-L4-02 | Status | GEF-L4-02 | SW02 | Level-7 | -
VSD Fault | GEF-L4-02-SW03 | Level-7 | GEF-L4-02 | VSD Fault | GEF-L4-02 | SW03 | Level-7 | -
VSD Speed Control | GEF-L4-02-SW04 | Level-7 | GEF-L4-02 | VSD Speed Control | GEF-L4-02 | SW04 | Level-7 | -
EDS - Sanitary Compartments
GEF-L4-03 | [7 empty] | VSD-GEF-L4-03
Enable | GEF-L4-03-SW01 | Level-7 | GEF-L4-03 | Enable | GEF-L4-03 | SW01 | Level-7 | -
Status | GEF-L4-03-SW02 | Level-7 | GEF-L4-03 | Status | GEF-L4-03 | SW02 | Level-7 | -
VSD Fault | GEF-L4-03-SW03 | Level-7 | GEF-L4-03 | VSD Fault | GEF-L4-03 | SW03 | Level-7 | -
VSD Speed Control | GEF-L4-03-SW04 | Level-7 | GEF-L4-03 | VSD Speed Control | GEF-L4-03 | SW04 | Level-7 | -
Ambulance Loading Dock
GEF-L4-05 | [7 empty] | VSD-GEF-L4-05
Enable | GEF-L4-05-SW01 | Level-7 | GEF-L4-05 | Enable | GEF-L4-05 | SW01 | Level-7 | -
Status | GEF-L4-05-SW02 | Level-7 | GEF-L4-05 | Status | GEF-L4-05 | SW02 | Level-7 | -
VSD Fault | GEF-L4-05-SW03 | Level-7 | GEF-L4-05 | VSD Fault | GEF-L4-05 | SW03 | Level-7 | -
VSD Speed Control | GEF-L4-05-SW04 | Level-7 | GEF-L4-05 | VSD Speed Control | GEF-L4-05 | SW04 | Level-7 | -
Garbage
GEF-L4/5/6/7 | [7 empty] | VSD-GEF-L4 to L7
Enable | GEF-L4/5/6/7-SW01 | Level-7 | GEF-L4/5/6/7 | Enable | GEF-L4/5/6/7 | SW01 | Level-7 | -
Status | GEF-L4/5/6/7-SW02 | Level-7 | GEF-L4/5/6/7 | Status | GEF-L4/5/6/7 | SW02 | Level-7 | -
VSD Fault | GEF-L4/5/6/7-SW03 | Level-7 | GEF-L4/5/6/7 | VSD Fault | GEF-L4/5/6/7 | SW03 | Level-7 | -
VSD Speed Control | GEF-L4/5/6/7-SW04 | Level-7 | GEF-L4/5/6/7 | VSD Speed Control | GEF-L4/5/6/7 | SW04 | Level-7 | -
GEF-L5-01 | [7 empty] | VSD-GEF-L5-01
Enable | GEF-L5-01-SW01 | Level-7 | GEF-L5-01 | Enable | GEF-L5-01 | SW01 | Level-7 | -
Status | GEF-L5-01-SW02 | Level-7 | GEF-L5-01 | Status | GEF-L5-01 | SW02 | Level-7 | -
VSD Fault | GEF-L5-01-SW03 | Level-7 | GEF-L5-01 | VSD Fault | GEF-L5-01 | SW03 | Level-7 | -
VSD Speed Control | GEF-L5-01-SW04 | Level-7 | GEF-L5-01 | VSD Speed Control | GEF-L5-01 | SW04 | Level-7 | -
Isolation Room 1
GEF-L5-02 | [7 empty] | VSD-GEF-L5-02
Enable | GEF-L5-02-SW01 | Level-7 | GEF-L5-02 | Enable | GEF-L5-02 | SW01 | Level-7 | -
Status | GEF-L5-02-SW02 | Level-7 | GEF-L5-02 | Status | GEF-L5-02 | SW02 | Level-7 | -
VSD Fault | GEF-L5-02-SW03 | Level-7 | GEF-L5-02 | VSD Fault | GEF-L5-02 | SW03 | Level-7 | -
VSD Speed Control | GEF-L5-02-SW04 | Level-7 | GEF-L5-02 | VSD Speed Control | GEF-L5-02 | SW04 | Level-7 | -
Isolation Room 1
GEF-L5-03 | [7 empty] | VSD-GEF-L5-03
Enable | GEF-L5-03-SW01 | Level-7 | GEF-L5-03 | Enable | GEF-L5-03 | SW01 | Level-7 | -
Status | GEF-L5-03-SW02 | Level-7 | GEF-L5-03 | Status | GEF-L5-03 | SW02 | Level-7 | -
VSD Fault | GEF-L5-03-SW03 | Level-7 | GEF-L5-03 | VSD Fault | GEF-L5-03 | SW03 | Level-7 | -
VSD Speed Control | GEF-L5-03-SW04 | Level-7 | GEF-L5-03 | VSD Speed Control | GEF-L5-03 | SW04 | Level-7 | -
Isolation Room 2
GEF-L5-04 | [7 empty] | VSD-GEF-L5-04
Enable | GEF-L5-04-SW01 | Level-7 | GEF-L5-04 | Enable | GEF-L5-04 | SW01 | Level-7 | -
Status | GEF-L5-04-SW02 | Level-7 | GEF-L5-04 | Status | GEF-L5-04 | SW02 | Level-7 | -
VSD Fault | GEF-L5-04-SW03 | Level-7 | GEF-L5-04 | VSD Fault | GEF-L5-04 | SW03 | Level-7 | -
VSD Speed Control | GEF-L5-04-SW04 | Level-7 | GEF-L5-04 | VSD Speed Control | GEF-L5-04 | SW04 | Level-7 | -
Isolation Room 2
GEF-L5-05 | [7 empty] | VSD-GEF-L5-05
Enable | GEF-L5-05-SW01 | Level-7 | GEF-L5-05 | Enable | GEF-L5-05 | SW01 | Level-7 | -
Status | GEF-L5-05-SW02 | Level-7 | GEF-L5-05 | Status | GEF-L5-05 | SW02 | Level-7 | -
VSD Fault | GEF-L5-05-SW03 | Level-7 | GEF-L5-05 | VSD Fault | GEF-L5-05 | SW03 | Level-7 | -
VSD Speed Control | GEF-L5-05-SW04 | Level-7 | GEF-L5-05 | VSD Speed Control | GEF-L5-05 | SW04 | Level-7 | -
Chiller Plantroom
GEF-L7-01 | [7 empty] | VSD-GEF-L7-01
Enable | GEF-L7-01-SW01 | Level-7 | GEF-L7-01 | Enable | GEF-L7-01 | SW01 | Level-7 | -
Status | GEF-L7-01-SW02 | Level-7 | GEF-L7-01 | Status | GEF-L7-01 | SW02 | Level-7 | -
VSD Fault | GEF-L7-01-SW03 | Level-7 | GEF-L7-01 | VSD Fault | GEF-L7-01 | SW03 | Level-7 | -
VSD Speed Control | GEF-L7-01-SW04 | Level-7 | GEF-L7-01 | VSD Speed Control | GEF-L7-01 | SW04 | Level-7 | -
Chiller Plantroom
OAF-L7-04 | [7 empty] | VSD-OAF-L7-04
Enable | OAF-L7-04-SW01 | Level-7 | OAF-L7-04 | Enable | OAF-L7-04 | SW01 | Level-7 | -
Status | OAF-L7-04-SW02 | Level-7 | OAF-L7-04 | Status | OAF-L7-04 | SW02 | Level-7 | -
VSD Fault | OAF-L7-04-SW03 | Level-7 | OAF-L7-04 | VSD Fault | OAF-L7-04 | SW03 | Level-7 | -
VSD Speed Control | OAF-L7-04-SW04 | Level-7 | OAF-L7-04 | VSD Speed Control | OAF-L7-04 | SW04 | Level-7 | -
GEF-L7-CR | [7 empty] | VSD-OAF-L7-04
Enable | GEF-L7-CR-SW01 | Level-7 | GEF-L7-CR | Enable | GEF-L7-CR | SW01 | Level-7 | -
Status | GEF-L7-CR-SW02 | Level-7 | GEF-L7-CR | Status | GEF-L7-CR | SW02 | Level-7 | -
VSD Fault | GEF-L7-CR-SW03 | Level-7 | GEF-L7-CR | VSD Fault | GEF-L7-CR | SW03 | Level-7 | -
VSD Speed Control | GEF-L7-CR-SW04 | Level-7 | GEF-L7-CR | VSD Speed Control | GEF-L7-CR | SW04 | Level-7 | -
Cooling Plant
CHW Plant |  | L7 East BMS Panel | [5 empty] | ECB600
Supply Water Temp | HLI-SW-01 | Level-7 | HLI | Supply Water Temp | HLI | SW-01 | Chiller 1/2
Return Water Temp | HLI-SW-02 | Level-7 | HLI | Return Water Temp | HLI | SW-02 | Chiller 1/2
Cooling demand | HLI-SW-03 | Level-7 | HLI | Cooling demand | HLI | SW-03 | Chiller 1/2
Setpoint | HLI-SW-04 | Level-7 | HLI | Setpoint | HLI | SW-04 | Chiller 1/2
Consumption | HLI-SW-05 | Level-7 | HLI | Load Limiting | HLI | SW-05 | Chiller 1/2
Faults | HLI-SW-06 | Level-7 | HLI | Faults | HLI | SW-06 | Chiller 1/2 | -
Current State | HLI-SW-07 | Level-7 | HLI | Current State | HLI | SW-07 | Chiller 1/2 | -
Current Load | HLI-SW-08 | Level-7 | HLI | Current Load | HLI | SW-08 | Chiller 1/2 | -
Load Limiting | HLI-SW-09 | Level-7 | HLI | Load Limiting | HLI | SW-09 | Chiller 1/2
Flow Status | HLI-SW-10 | Level-7 | HLI | Flow Status | HLI | SW-10 | Chiller 1/2
Head Pressure | HLI-SW-11 | Level-7 | HLI | Head Pressure | HLI | SW-11 | Chiller 1/2
Suction Pressure | HLI-SW-12 | Level-7 | HLI | Suction Pressure | HLI | SW-12 | Chiller 1/2
Energy Meter | Energy Meter-SW-13 | Level-7 | Energy Meter | Energy Meter | Energy Meter | SW-13 | Level-7 | Energy meter
IO-DIM6-1 |  | Level-7 |  | IO-DIM6-1 |  | UI-1 |  | IO-DIM6
CHW-PP-01 Status | CHW Plant-UI-1 | Level-7 | CHW Plant | CHW-PP-01 Status | CHW Plant |  | Level-7 | SFS-1
CHW-PP-02 Status |  | Level-7 | CHW Plant | CHW-PP-02 Status | CHW Plant |  | Level-7 | SFS-1
CHW-SP-01 Status |  | Level-7 | CHW Plant | CHW-SP-01 Status | CHW Plant |  | Level-7 | SFS-1
CHW-SP-02 Status |  | Level-7 | CHW Plant | CHW-SP-02 Status | CHW Plant |  | Level-7 | SFS-1
Chem Treatment Alarm 1 | CHW Plant-UI-4 | Level-7 | CHW Plant | Chem Treatment Alarm 1 | CHW Plant | UI-4 | Level-7 | Terminals
Chem Treatment Alarm 2 | CHW Plant-UI-4 | Level-7 | CHW Plant | Chem Treatment Alarm 2 | CHW Plant | UI-4 | Level-7 | Terminals
IO-DIM6-2 |  | Level-7 |  | IO-DIM6-2 |  | UI-2 |  | IO-DIM6
CH1 Chiller Status | CHW Plant- | Level-7 | CHW Plant | CH1 Chiller Status | CHW Plant |  | Level-7 | Terminals
CH2 Chiller Status | CHW Plant- | Level-7 | CHW Plant | CH2 Chiller Status | CHW Plant |  | Level-7 | Terminals
CH1 Chiller General Fault | CHW Plant- | Level-7 | CHW Plant | CH1 Chiller General Fault | CHW Plant |  | Level-7 | Terminals
CH2 Chiller General Fault | CHW Plant- | Level-7 | CHW Plant | CH2 Chiller General Fault | CHW Plant |  | Level-7 | Terminals
Leak Detector CH1 | CHW Plant-UI-3 | Level-7 | CHW Plant | Leak Detector CH1 | CHW Plant | UI-3 | Level-7 | Terminals
Leak Detector CH2 | CHW Plant-UI-4 | Level-7 | CHW Plant | Leak Detector CH2 | CHW Plant | UI-4 | Level-7 | Terminals
Chiller 1 Evaporator DP | CHW Plant-UI-5 | Level-7 | CHW Plant | Chiller 1 Evaporator DP | CHW Plant | UI-5 | Level-7 | QBE3000-D1
Chiller 2 Evaporator DP | CHW Plant-UI-6 | Level-7 | CHW Plant | Chiller 2 Evaporator DP | CHW Plant | UI-6 | Level-7 | QBE3000-D1
System DP | CHW Plant-UI-7 | Level-7 | CHW Plant | System DP | CHW Plant | UI-7 | Level-7 | QBE3000-D4
Secondary CHW Flow | CHW Plant-UI-8 | Level-7 | CHW Plant | Secondary CHW Flow | CHW Plant | UI-8 | Level-7 | Flow meter
Decoupler CHW Flow | CHW Plant-UI-9 | Level-7 | CHW Plant | Decoupler CHW Flow | CHW Plant | UI-9 | Level-7 | Flow meter
Secondary CHW Supply Temp | CHW Plant-UI-10 | Level-7 | CHW Plant | Secondary CHW Supply Temp | CHW Plant | UI-10 | Level-7 | PDIGR-TE200CE24C2E + well
Secondary CHW Return Temp | CHW Plant-UI-11 | Level-7 | CHW Plant | Secondary CHW Return Temp | CHW Plant | UI-11 | Level-7 | PDIGR-TE200CE24C2E + well
Decoupler CHW Temp | CHW Plant-UI-12 | Level-7 | CHW Plant | Decoupler CHW Temp | CHW Plant | UI-12 | Level-7 | PDIGR-TE200CE24C2E + well
Tank Low CHW Temp | CHW Plant-UI-13 | Level-7 | CHW Plant | Tank Low CHW Temp | CHW Plant | UI-13 | Level-7 | PDIGR-TE200CE24C2E + well
Tank High CHW Temp | CHW Plant-UI-14 | Level-7 | CHW Plant | Tank High CHW Temp | CHW Plant | UI-14 | Level-7 | PDIGR-TE200CE24C2E + well
Chiller 1 Condenser DP | CHW Plant-UI-15 | Level-7 | CHW Plant | Chiller 1 Condenser DP | CHW Plant | UI-15 | Level-7 | QBE3000-D1
Chiller 2 Condenser DP | CHW Plant-UI-16 | Level-7 | CHW Plant | Chiller 2 Condenser DP | CHW Plant | UI-16 | Level-7 | QBE3000-D1
CH1 Chiller Enable | CHW Plant-UO-1 | Level-7 | CHW Plant | CH1 Chiller Enable | CHW Plant | UO-1 | Level-7 | 12VDC Relay
CH2 Chiller Enable | CHW Plant-UO-2 | Level-7 | CHW Plant | CH2 Chiller Enable | CHW Plant | UO-2 | Level-7 | 12VDC Relay
CHW Bypass Valve | CHW Plant-UO-3 | Level-7 | CHW Plant | CHW Bypass Valve | CHW Plant | UO-3 | Level-7 | CHWV Actuator
CHW Plant Extension | [7 empty] | ECX400
CW-P-01 Status | CHW Plant-UI-1 | Level-7 | CHW Plant | CW-P-01 Status | CHW Plant | UI-1 | Level-7 | SFS-1
CW-P-02 Status | CHW Plant-UI-2 | Level-7 | CHW Plant | CW-P-02 Status | CHW Plant | UI-2 | Level-7 | SFS-1
CT 1 Cell 1 Sump Temp | CHW Plant-UI-3 | Level-7 | CHW Plant | CT 1 Cell 1 Sump Temp | CHW Plant | UI-3 | Level-7 | PDIGR-TE200CE24C2E + well
CT 1 Cell 2 Sump Temp | CHW Plant-UI-4 | Level-7 | CHW Plant | CT 1 Cell 2 Sump Temp | CHW Plant | UI-4 | Level-7 | PDIGR-TE200CE24C2E + well
CT Common Leave Temp | CHW Plant-UI-5 | Level-7 | CHW Plant | CT Common Leave Temp | CHW Plant | UI-5 | Level-7 | PDIGR-TE200CE24C2E + well
CT1 Cell1 Enter CW Iso Valve | CHW Plant-UO-1 | Level-7 | CHW Plant | CT1 Cell1 Enter CW Iso Valve | CHW Plant | UO-1 | Level-7 | CWV Actuator
CT1 Cell1 Leave CW Iso Valve | CHW Plant-UO-2 | Level-7 | CHW Plant | CT1 Cell1 Leave CW Iso Valve | CHW Plant | UO-2 | Level-7 | CWV Actuator
CT1 Cell2 Enter CW Iso Valve | CHW Plant-UO-3 | Level-7 | CHW Plant | CT1 Cell2 Enter CW Iso Valve | CHW Plant | UO-3 | Level-7 | CWV Actuator
CT1 Cell2 Leave CW Iso Valve | CHW Plant-UO-4 | Level-7 | CHW Plant | CT1 Cell2 Leave CW Iso Valve | CHW Plant | UO-4 | Level-7 | CWV Actuator
CTs CW Bypass Valve | CHW Plant-UO-5 | Level-7 | CHW Plant | CTs CW Bypass Valve | CHW Plant | UO-5 | Level-7 | CWV Actuator
CHW-SP-01 | [7 empty] | VSD-CHW-SP-01
Enable | CHW-SP-01-SW01 | Level-7 | CHW-SP-01 | Enable | CHW-SP-01 | SW01 | Level-7 | -
Status | CHW-SP-01-SW02 | Level-7 | CHW-SP-01 | Status | CHW-SP-01 | SW02 | Level-7 | -
VSD Fault | CHW-SP-01-SW03 | Level-7 | CHW-SP-01 | VSD Fault | CHW-SP-01 | SW03 | Level-7 | -
VSD Speed Control | CHW-SP-01-SW04 | Level-7 | CHW-SP-01 | VSD Speed Control | CHW-SP-01 | SW04 | Level-7 | -
CHW-SP-02 | [7 empty] | VSD-CHW-SP-02
Enable | CHW-SP-02-SW01 | Level-7 | CHW-SP-02 | Enable | CHW-SP-02 | SW01 | Level-7 | -
Status | CHW-SP-02-SW02 | Level-7 | CHW-SP-02 | Status | CHW-SP-02 | SW02 | Level-7 | -
VSD Fault | CHW-SP-02-SW03 | Level-7 | CHW-SP-02 | VSD Fault | CHW-SP-02 | SW03 | Level-7 | -
VSD Speed Control | CHW-SP-02-SW04 | Level-7 | CHW-SP-02 | VSD Speed Control | CHW-SP-02 | SW04 | Level-7 | -
CHW-PP-01 | [7 empty] | VSD-CHW-PP-01
Enable | CHW-PP-01-SW01 | Level-7 | CHW-PP-01 | Enable | CHW-PP-01 | SW01 | Level-7 | -
Status | CHW-PP-01-SW02 | Level-7 | CHW-PP-01 | Status | CHW-PP-01 | SW02 | Level-7 | -
VSD Fault | CHW-PP-01-SW03 | Level-7 | CHW-PP-01 | VSD Fault | CHW-PP-01 | SW03 | Level-7 | -
VSD Speed Control | CHW-PP-01-SW04 | Level-7 | CHW-PP-01 | VSD Speed Control | CHW-PP-01 | SW04 | Level-7 | -
CHW-PP-02 | [7 empty] | VSD-CHW-PP-02
Enable | CHW-PP-02-SW01 | Level-7 | CHW-PP-02 | Enable | CHW-PP-02 | SW01 | Level-7 | -
Status | CHW-PP-02-SW02 | Level-7 | CHW-PP-02 | Status | CHW-PP-02 | SW02 | Level-7 | -
VSD Fault | CHW-PP-02-SW03 | Level-7 | CHW-PP-02 | VSD Fault | CHW-PP-02 | SW03 | Level-7 | -
VSD Speed Control | CHW-PP-02-SW04 | Level-7 | CHW-PP-02 | VSD Speed Control | CHW-PP-02 | SW04 | Level-7 | -
CW-P-01 | [7 empty] | VSD-CW-P-01
Enable | CW-P-01-SW01 | Level-7 | CW-P-01 | Enable | CW-P-01 | SW01 | Level-7 | -
Status | CW-P-01-SW02 | Level-7 | CW-P-01 | Status | CW-P-01 | SW02 | Level-7 | -
VSD Fault | CW-P-01-SW03 | Level-7 | CW-P-01 | VSD Fault | CW-P-01 | SW03 | Level-7 | -
VSD Speed Control | CW-P-01-SW04 | Level-7 | CW-P-01 | VSD Speed Control | CW-P-01 | SW04 | Level-7 | -
CW-P-02 | [7 empty] | VSD-CW-P-02
Enable | CW-P-02-SW01 | Level-7 | CW-P-02 | Enable | CW-P-02 | SW01 | Level-7 | -
Status | CW-P-02-SW02 | Level-7 | CW-P-02 | Status | CW-P-02 | SW02 | Level-7 | -
VSD Fault | CW-P-02-SW03 | Level-7 | CW-P-02 | VSD Fault | CW-P-02 | SW03 | Level-7 | -
VSD Speed Control | CW-P-02-SW04 | Level-7 | CW-P-02 | VSD Speed Control | CW-P-02 | SW04 | Level-7 | -
| - |  | 0 |  |  |  |  | -
CT-F-01 | [7 empty] | VSD-CT-F-01
Enable | CT-F-01-SW01 | Level-7 | CT-F-01 | Enable | CT-F-01 | SW01 | Level-7 | -
Status | CT-F-01-SW02 | Level-7 | CT-F-01 | Status | CT-F-01 | SW02 | Level-7 | -
VSD Fault | CT-F-01-SW03 | Level-7 | CT-F-01 | VSD Fault | CT-F-01 | SW03 | Level-7 | -
VSD Speed Control | CT-F-01-SW04 | Level-7 | CT-F-01 | VSD Speed Control | CT-F-01 | SW04 | Level-7 | -
CT-F-02 | [7 empty] | VSD-CT-F-02
Enable | CT-F-02-SW01 | Level-7 | CT-F-02 | Enable | CT-F-02 | SW01 | Level-7 | -
Status | CT-F-02-SW02 | Level-7 | CT-F-02 | Status | CT-F-02 | SW02 | Level-7 | -
VSD Fault | CT-F-02-SW03 | Level-7 | CT-F-02 | VSD Fault | CT-F-02 | SW03 | Level-7 | -
VSD Speed Control | CT-F-02-SW04 | Level-7 | CT-F-02 | VSD Speed Control | CT-F-02 | SW04 | Level-7 | -
Heating Plant
HW Plant |  | L7 HWG Panel | [5 empty] | ECB600
HW-PP-01 Status | HW Plant -UI-1 | Level-7 | HW Plant | HW-PP-01 Status | HW Plant | UI-1 | Level-7 | SFS-1
HW-PP-02 Status | HW Plant -UI-2 | Level-7 | HW Plant | HW-PP-02 Status | HW Plant | UI-2 | Level-7 | SFS-1
HW-SP-01 Status | HW Plant -UI-3 | Level-7 | HW Plant | HW-SP-01 Status | HW Plant | UI-3 | Level-7 | SFS-1
HW-SP-02 Status | HW Plant -UI-4 | Level-7 | HW Plant | HW-SP-02 Status | HW Plant | UI-4 | Level-7 | SFS-1
Boiler 1 DP | HW Plant -UI-5 | Level-7 | HW Plant | Boiler 1 DP | HW Plant | UI-5 | Level-7 | QBE3000-D1
Boiler 2 DP | HW Plant -UI-6 | Level-7 | HW Plant | Boiler 2 DP | HW Plant | UI-6 | Level-7 | QBE3000-D1
System DP | HW Plant -UI-7 | Level-7 | HW Plant | System DP | HW Plant | UI-7 | Level-7 | QBE3000-D4
Secondary HW Flow | HW Plant -UI-8 | Level-7 | HW Plant | Secondary HW Flow | HW Plant | UI-8 | Level-7 | Flow meter
Decoupler HW Flow | HW Plant -UI-9 | Level-7 | HW Plant | Decoupler HW Flow | HW Plant | UI-9 | Level-7 | Flow meter
Secondary HW Supply Temp | HW Plant -UI-10 | Level-7 | HW Plant | Secondary HW Supply Temp | HW Plant | UI-10 | Level-7 | PDIGR-TE200CE24C2E + well
Decoupler HW Temp | HW Plant -UI-11 | Level-7 | HW Plant | Decoupler HW Temp | HW Plant | UI-11 | Level-7 | PDIGR-TE200CE24C2E + well
Secondary HW Return Temp | HW Plant -UI-14 | Level-7 | HW Plant | Secondary HW Return Temp | HW Plant | UI-14 | Level-7 | PDIGR-TE200CE24C2E + well
Gas Solenoid Valve Interlock | HW Plant -UI-15 | Level-7 | HW Plant | Gas Solenoid Valve Interlock | HW Plant | UI-15 | Level-7 | Terminals
Bypass Valve | HW Plant -UO-1 | Level-7 | HW Plant | Bypass Valve | HW Plant | UO-1 | Level-7 | CHWV Actuator
Boiler 1 Enable | HW Plant -UO-2 | Level-7 | HW Plant | Boiler 1 Enable | HW Plant | UO-2 | Level-7 | 12VDC Relay
Boiler 2 Enable | HW Plant -UO-3 | Level-7 | HW Plant | Boiler 2 Enable | HW Plant | UO-3 | Level-7 | 12VDC Relay
Boiler 1 Setpoint | HW Plant -UO-4 | Level-7 | HW Plant | Boiler 1 Setpoint | HW Plant | UO-4 | Level-7 | Terminals
Boiler 2 Setpoint | HW Plant -UO-5 | Level-7 | HW Plant | Boiler 2 Setpoint | HW Plant | UO-5 | Level-7 | Terminals
HW Plant IO Expansion | [7 empty] | ECX420
Boiler 1 Supply Water Temp | HW Plant -UI-1 | Level-7 | HW Plant IO Expansion | Boiler 1 Supply Water Temp | HW Plant | UI-1 | Level-7 | PDIGR-TE200CE24C2E + well
Boiler 1 Return Water Temp | HW Plant -UI-2 | Level-7 | HW Plant IO Expansion | Boiler 1 Return Water Temp | HW Plant | UI-2 | Level-7 | PDIGR-TE200CE24C2E + well
Boiler 1 Flow Status | HW Plant -UI-3 | Level-7 | HW Plant IO Expansion | Boiler 1 Flow Status | HW Plant | UI-3 | Level-7 | Terminals
Boiler 1 Fault | HW Plant -UI-4 | Level-7 | HW Plant IO Expansion | Boiler 1 Fault | HW Plant | UI-4 | Level-7 | Terminals
Boiler 2 Supply Water Temp | HW Plant -UI-5 | Level-7 | HW Plant IO Expansion | Boiler 2 Supply Water Temp | HW Plant | UI-5 | Level-7 | PDIGR-TE200CE24C2E + well
Boiler 2 Return Water Temp | HW Plant -UI-6 | Level-7 | HW Plant IO Expansion | Boiler 2 Return Water Temp | HW Plant | UI-6 | Level-7 | PDIGR-TE200CE24C2E + well
Boiler 2 Flow Status | HW Plant -UI-7 | Level-7 | HW Plant IO Expansion | Boiler 2 Flow Status | HW Plant | UI-7 | Level-7 | Terminals
Boiler 2 Fault | HW Plant -UI-8 | Level-7 | HW Plant IO Expansion | Boiler 2 Fault | HW Plant | UI-8 | Level-7 | Terminals
Boiler 1 A/O/M Switch Auto | HW Plant -UI-9 | Level-7 | HW Plant IO Expansion | Boiler 1 A/O/M Switch Auto | HW Plant | UI-9 | Level-7 | Terminals
Boiler 1 A/O/M Switch Manual | HW Plant -UI-10 | Level-7 | HW Plant IO Expansion | Boiler 1 A/O/M Switch Manual | HW Plant | UI-10 | Level-7 | Terminals
Boiler 2 A/O/M Switch Auto | HW Plant -UI-11 | Level-7 | HW Plant IO Expansion | Boiler 2 A/O/M Switch Auto | HW Plant | UI-11 | Level-7 | Terminals
Boiler 2 A/O/M Switch Manual | HW Plant -UI-12 | Level-7 | HW Plant IO Expansion | Boiler 2 A/O/M Switch Manual | HW Plant | UI-12 | Level-7 | Terminals
HHW-SP-01 | [7 empty] | VSD-HHW-SP-01
Enable | HHW-SP-01-SW01 | Level-7 | HHW-SP-01 | Enable | HHW-SP-01 | SW01 | Level-7 | -
Status | HHW-SP-01-SW02 | Level-7 | HHW-SP-01 | Status | HHW-SP-01 | SW02 | Level-7 | -
VSD Fault | HHW-SP-01-SW03 | Level-7 | HHW-SP-01 | VSD Fault | HHW-SP-01 | SW03 | Level-7 | -
VSD Speed Control | HHW-SP-01-SW04 | Level-7 | HHW-SP-01 | VSD Speed Control | HHW-SP-01 | SW04 | Level-7 | -
HHW-SP-02 | [7 empty] | VSD-HHW-SP-02
Enable | HHW-SP-02-SW01 | Level-7 | HHW-SP-02 | Enable | HHW-SP-02 | SW01 | Level-7 | -
Status | HHW-SP-02-SW02 | Level-7 | HHW-SP-02 | Status | HHW-SP-02 | SW02 | Level-7 | -
VSD Fault | HHW-SP-02-SW03 | Level-7 | HHW-SP-02 | VSD Fault | HHW-SP-02 | SW03 | Level-7 | -
VSD Speed Control | HHW-SP-02-SW04 | Level-7 | HHW-SP-02 | VSD Speed Control | HHW-SP-02 | SW04 | Level-7 | -
HHW-PP-01 | [7 empty] | VSD-HHW-PP-01
Enable | HHW-PP-01-SW01 | Level-7 | HHW-PP-01 | Enable | HHW-PP-01 | SW01 | Level-7 | -
Status | HHW-PP-01-SW02 | Level-7 | HHW-PP-01 | Status | HHW-PP-01 | SW02 | Level-7 | -
VSD Fault | HHW-PP-01-SW03 | Level-7 | HHW-PP-01 | VSD Fault | HHW-PP-01 | SW03 | Level-7 | -
VSD Speed Control | HHW-PP-01-SW04 | Level-7 | HHW-PP-01 | VSD Speed Control | HHW-PP-01 | SW04 | Level-7 | -
HHW-PP-02 | [7 empty] | VSD-HHW-PP-02
Enable | HHW-PP-02-SW01 | Level-7 | HHW-PP-02 | Enable | HHW-PP-02 | SW01 | Level-7 | -
Status | HHW-PP-02-SW02 | Level-7 | HHW-PP-02 | Status | HHW-PP-02 | SW02 | Level-7 | -
VSD Fault | HHW-PP-02-SW03 | Level-7 | HHW-PP-02 | VSD Fault | HHW-PP-02 | SW03 | Level-7 | -
VSD Speed Control | HHW-PP-02-SW04 | Level-7 | HHW-PP-02 | VSD Speed Control | HHW-PP-02 | SW04 | Level-7 | -

## Hardware
Part | Supplier | Qty | Termination |  | Application | Cable | Power Consumption (VA)
Veris |  | #REF!
CHWV Actuator | TBA | #REF! |  |  |  | Shielded twisted 3 core (Electra 7303C)
CWV Actuator | TBA | #REF! |  |  |  | Shielded twisted 3 core (Electra 7303C)
HHWV Actuator | TBA | #REF! |  |  |  | Shielded twisted 3 core (Electra 7303C)
Enthalpy | Vasalia | #REF!
Vaccume Tx
PT-015 (WS) |  | #REF! | Wet Switch
Pressure Tx
HD2XVCTK (T) | Veris | #REF! | Signal orange, Com black | Duct temp & RH
HD2XVCTK (H) | Veris | #REF! | Signal blue, Com black, 24VAC red | Duct temp & RH
HO3XVSTK | Veris | #REF! | Blue Humidity, Com black, 24VAC red, Orange thermister | Duct temp & RH |  | Shielded twisted 3 core (Electra 7303C) and Shielded twisted pair (Electra 7301P)
PXPLX02C | Veris | #REF! | Signal, Com, 24V terminals | Dry DP high range | Duct static
PXPXX02C | Veris | #REF! | Signal, Com, 24V terminals | Dry DP high range | Duct static
PXPXX01C | Veris | #REF! | Signal, Com, 24V terminals | Dry DP low range | Space & stair press
PWLX06C | Veris | #REF! | Signal, Com, 24V terminals | Wet DP | Chiller dp | Shielded twisted 3 core (Electra 7303C)
PWLX08C | Veris | #REF! | Signal, Com, 24V terminals | Wet DP | Differential Pressure | Shielded twisted 3 core (Electra 7303C)
HWX2XCTK (H) | Veris | #REF! | Signal, Com, 24VAC terminals | Space RH & temp | ICU | Shielded twisted 3 core (Electra 7303C)
HWX2XCTK (T) | Veris | #REF! | Signal , Com Terminals | Space RH & temp | ICU | Shielded twisted pair (Electra 7301P)
HD3XVCX | Veris | #REF! | Signal blue, Com black, 24VAC red | Duct RH | RA RH | Shielded twisted 3 core (Electra 7303C)
H800 | Veris | #REF! | Connect pair | Solid Core Fixed Trip |  | Shielded twisted pair (Electra 7301P)
H608 | Veris | #REF! | Connect pair | Split Core Variable Trip |  | Shielded twisted pair (Electra 7301P)
H600 | Veris | #REF! | Connect pair | Split Core Fixed trip |  | Shielded twisted pair (Electra 7301P)
H221 | Veris | #REF! | White +, Black - | Slpit Core Amps |  | Shielded twisted pair (Electra 7301P)
H321 | - |  |  |  |  | Shielded twisted pair (Electra 7301P)
EPP102-LCD | - |  |  |  | Duct static | Shielded twisted 3 core (Electra 7303C) |  | PXPLX02C
EPP102 | Veris | #REF! | Signal, Com, 24V terminals | Dry DP high range | Duct static | Shielded twisted 3 core (Electra 7303C) |  | PXPXX02C
EPP101-LCD | Veris | #REF! | Signal, Com, 24V terminals | Dry DP low range | Space & stair press | Shielded twisted 3 core (Electra 7303C) |  | PXPLX01C
EPP101 | Veris | #REF! | Signal, Com, 24V terminals | Dry DP low range | Space & stair press | Shielded twisted 3 core (Electra 7303C) |  | PXPXX01C
Wago
750-430 | Wago 8 Digital Input slots $141.47 | 750-430 | Wago 8 Digital Input slots $141.47 | DI Module 8 inputs
750-600 Wago End Module $33.26 | Wago End Module $33.26 | 750-600 Wago End Module $33.26 | Wago End Module $33.26 | DI Module Interface
Siemens
SSR Module | Siemens | #REF! | Signal U1, Com M, 24VAC G |  |  | Shielded twisted 3 Pair (Electra 7303P)
Flow meter |  | #REF!
Energy meter |  | #REF!
QVM62.1 | Siemens | #REF! | Signal U1, Com M, 24VAC G | Velocity sensor |  | Shielded twisted 3 Pair (Electra 7303P)
QFM2160 Temp | Siemens | #REF! | Temp Signal U2, 24VAC G, Neutral GO | Combined OA and Hum Sensor |  | Shielded twisted 3 Pair (Electra 7303P) | 1
QFM2160 Humidity | Siemens | #REF! | Humidity Signal U1 | Combined OA and Hum Sensor |  | Shielded twisted 3 Pair (Electra 7303P) | 1
AT-02-1110-0 | Siemens | #REF! | Signal 4, 24VDC 3 | CO sensor
SQS65 | Siemens | #REF! | Signal, Com, 24VAC terminals
SQX62 | Siemens | #REF! | Signal, Com, 24VAC terminals |  |  | Shielded twisted 3 Pair (Electra 7303P)
SKB60 | Siemens | #REF! | Signal, Com, 24VAC terminals
SSB61 | Siemens | #REF! | Signal grey 8, Com black 2, 24VAC red 1 |  |  | 2 core AirCon Cable (Electra AC7502) and Shielded twisted pair (Electra 7301P) | 2
SSC61 | Siemens | #REF! | Signal, Com, 24VAC terminals
SKC60 | Siemens | #REF! | Signal, Com, 24VAC terminals
GPA161.1E | Siemens | #REF! | Signal grey 8, Com black 2, 24VAC red 1
GDB161.1E | Siemens | #REF! | Signal grey 8, Com black 2, 24VAC red 2 |  |  | Shielded twisted 3 Pair (Electra 7303P)
GQD161.1A | Siemens | #REF!
GMA161.1E | Siemens | #REF!
GMA321.1E | Siemens | #REF!
TBA CHW actuator | Siemens | #REF! | Signal, Com, 24VAC terminals |  | CHW bypass
TBA HW actuator | Siemens | #REF! | Signal, Com, 24VAC terminals |  | HW bypass
UA9 | Siemens | #REF! |  |  |  | Shielded twisted pair (Electra 7301P)
WM271MRP | Siemens | #REF! | Connect Pair | Water Meter |  | Shielded twisted pair (Electra 7301P)
SBTFDK.085U1018 | Siemens | #REF! | Signal, Com, 24VAC terminals | Magflow Signal Converter |  | Shielded twisted 3 Pair (Electra 7303P)
GIB161.1E | Siemens | #REF! | Signal grey 8, Com black 2, 24VAC red 1 | Damper Actuator |  | 2 core AirCon Cable (Electra AC7502) and Shielded twisted pair (Electra 7301P) | 6
GBB161.1E | Siemens | #REF! | Signal grey 8, Com black 2, 24VAC red 1 | Damper Actuator |  | 2 core AirCon Cable (Electra AC7502) and Shielded twisted pair (Electra 7301P) | 4
QPM-2102 (CO2) | Siemens | #REF! | CO2 Signal | Combined CO2 and VOC Sensor | Duct Sensor | Shielded twisted 3 Pair (Electra 7302P)
QPM-2102 (VOC) | Siemens | #REF! | VOC Signal | Combined CO2 and VOC Sensor | Duct Sensor | Shielded twisted 3 Pair (Electra 7302P)
QBM2030-1U | Siemens | #REF! | Stairwell Static Pressure | Duct Static Pressure | Stair Pressure | Shielded twisted 3 Pair (Electra 7302P)
QBM2030-5 | Siemens | #REF! | Duct Static Pressure | Duct Static Pressure | Duct Sensor | Shielded twisted 3 Pair (Electra 7302P)
QBM2030-30 | Siemens | #REF!
QBE3000-D1 | Siemens | #REF! | Signal, Com, 24VAC terminals | Water Diff Pressure sensor | 0-1bar | Shielded twisted 3 core (Electra 7303C)
QBE3000-D4 | Siemens | #REF! | Signal, Com, 24VAC terminals | Water Diff Pressure sensor | 0-4bar | Shielded twisted 3 core (Electra 7303C)
QFA3160 | Siemens |  | space temp 10VDC, RH 10VDC | Combo sensor |  | Shielded twisted 3 core (Electra 7303C)
Schneider
WFS-25AB | TAC | #REF! | N.O. & Com terminals
TS-6721-853 | TAC | #REF! | Connect pair |  | Immersion Sensor | Shielded twisted pair (Electra 7301P)
SFS-1 | TAC | #REF! | Comm Blue, NO Marrone | Water DP Switch |  | Shielded twisted pair (Electra 7301P)
0-047-0106-0 | TAC | #REF! | 2 N.O. & 3 Com terminals | Filter status |  | Shielded twisted pair (Electra 7301P)
930.8 | - |  |  |  |  | Shielded twisted pair (Electra 7301P)
TSMN-57011-850 | - |  |  |  | Space temp | Shielded twisted pair (Electra 7301P)
TS-6721-850 | TAC | #REF! | Connect pair |  | Duct temp | Shielded twisted pair (Electra 7301P)
MN-S2 | TAC | #REF! | Connect pair |  | Space Temp | Shielded twisted pair (Electra 7301P)
MN-S1HT | TAC | #REF! | Connect Pair |  | Space Temp & Humidity | Shielded twisted pair (Electra 7301P)
Belimo
TR24.SR | Belimo | #REF! | Signal White Y, 24VAC Red 2, Comm Black 1 | Ball Valve Actuator |  | Shielded twisted 3 core (Electra 7303C)
KM 24-3 (Existing) | Belimo | #REF! | Comm Black 1, White Open 2, Red Close 3 | VAV Damper Actuator |  | Shielded twisted 3 core (Electra 7303C)
AF24-SR | Belimo | #REF! | Signal White 3, 24VAC Red 2, Comm Black 1 | Damper Actuator Spring Return |  | Shielded twisted 3 core (Electra 7303C)
SRU24-SR | Belimo | #REF! | Signal White 3, 24VAC Red 2, Comm Black 1 | Ball Valve Actuator |  | Shielded twisted 3 core (Electra 7303C)
LRU24-SR | Belimo | #REF! | Signal White 3, 24VAC Red 2, Comm Black 1 | Ball Valve Actuator |  | Shielded twisted 3 core (Electra 7303C)
Honeywell
Actuator Terminals | Honeywell |  | Signal - F, Comm - T2 |  |  | Shielded twisted pair (Electra 7301P) | 1.8
ML7421B1023-E | Honeywell | #REF! | Signal - Plus, 24VAC - T1, Comm - T2 |  |  | Shielded twisted 3 core (Electra 7303C) | 7
M7410E1002 | Honeywell | #REF! | Signal - Green, 24VAC - Brown, Comm - White | Valve Actuator |  | Shielded twisted 3 core (Electra 7303C)
ML7420A6033-E | Honeywell | #REF! | Signal - Plus, Signal Com - Minus, 24VAC - T1, Comm - T2 | Valve Actuator |  | Shielded twisted 3 core (Electra 7303C)
CS7510A2008 | -
CS7520A2007 | -
Dwyer
CCS | Dwyer | #REF! | -46 | Current Switch |  | Shielded twisted pair (Electra 7301P)
GSTA | Dwyer | #REF! | Signal White 3, 24VAC Red 2, Comm Black 4 | CO Sensor |  | Shielded twisted 3 core (Electra 7303C)
CDW | Dwyer | #REF! | Signal White 2, 24VAC Red 3, Comm Black 1 | CO2 Sensor |  | Shielded twisted 3 core (Electra 7303C)
CDD | Dwyer | #REF! | Signal White 2, 24VAC Red 3, Comm Black 2 | CO2 Sensor |  | Shielded twisted 3 core (Electra 7303C)
AFS - 930.80222524 | Dwyer | #REF! | white = signal, black = Common | 0-500Pa Air Switch | Fan Status | 1 pair 7/0.30 shielded twisted cable (Electra 7301p)
Other
12VDC Relay |  | #REF! | Terminals in MSSB |  |  | Panel Wire
24VAC Relay |  | #REF! | Terminals in MSSB |  |  | Panel Wire
Lighting 24VAC Relay |  | #REF! | Terminals in DB |  |  | Shielded twisted pair (Electra 7301P)
Terminals |  | #REF! | Terminals in MSSB |  |  | Shielded twisted pair (Electra 7301P)
VSD Terminals |  | #REF! | Terminals in VSD |  |  | Shielded twisted pair (Electra 7301P)
Lift Terminals |  | #REF! | Terminals in Lift |  |  | Shielded twisted pair (Electra 7301P)
Walkway Terminals |  | #REF! | Terminals in Walkway |  |  | Shielded twisted pair (Electra 7301P)
AHU Terminals |  | #REF! | Terminals in AHU Controller |  |  | Shielded twisted pair (Electra 7301P)
FCU Terminals |  | #REF! | Terminals in FCU |  |  | Shielded twisted pair (Electra 7301P)
IO-RM3 | - | #REF! | RM3 3 Relay Module |  |  | Shielded twisted pair (Electra 7301P)
HWH Terminals | - | #REF! | Terminals in HWH |  |  | Shielded twisted pair (Electra 7301P)
Unit Terminals |  | #REF! | Terminals in Unit |  |  | Shielded twisted pair (Electra 7301P)
IO-DIM6 | Sontay | #REF! | DIM6 Input Multiplexer |  |  | Shielded twisted pair (Electra 7301P)
Pushbutton |  | #REF! | Connect Pair |  |  | Shielded twisted pair (Electra 7301P)
Green Neon |  | #REF! | Switched 24VAC |  |  | 2 core AirCon Cable (Electra AC7502)
Rocker Switch |  | #REF! | Connect Pair |  |  | Shielded twisted pair (Electra 7301P)
0-10VDC Relay |  | #REF! | Signal White +, Signal Comm Black - across coil |  |  | Shielded twisted pair (Electra 7301P)
07KIT-RELAYUNDI | Distech | #REF! | Distech UO Relay |  |  | Shielded twisted pair (Electra 7301P)
MA-0-1110-A-8 | MSR | #REF! | CO Car Park Sensor
Existing Temperature |  | #REF! | Connect pair | Existing Sensor |  | Shielded twisted pair (Electra 7301P) | 1
CDD | Dwyer | #REF! | Signal, Com, 24VAC terminals | CO2 Sensor | Duct Sensor | Shielded twisted 3 core (Electra 7303C)
TE-702-B-12-C | Mamac | #REF! | Connect pair |  | Duct temp | Shielded twisted pair (Electra 7301P)
TBA |  | #REF! | To Be Advised | To Be Advised | To Be Advised | To Be Advised
Motion Detector (OC-C-LV) | Sontay | #REF! | To Be Advised | To Be Advised | To Be Advised | To Be Advised
QLS60 Siemens Solar glare
GAS-CO2-0xx-A | Gas Alarm | #REF! | Signal, Com, 24VAC terminals | CO2 Sensor | Wall Sensor | Shielded twisted 3 core (Electra 7303C)
Distech
EC-Sensor | [5 empty] | 1 pair 7/0.30 shielded twisted cable (Electra 7301p)
EC-Smart-Vue | Distech | #REF! | RJ45 Plug - terminate using TIA/EIA-568-A | Communicating Sensor |  | Cat5e Cable daisy chained between each sensor and controller
PDIGR-TE200CE24B2E | Distech | #REF! | white = signal, black = Common | Immersion Pipe Sensor |  | 1 pair 7/0.30 shielded twisted cable (Electra 7301p)
PDIGR-TE200BE24B2 | Distech | #REF! | white = signal, black = Common | Immersion Pipe Sensor |  | 1 pair 7/0.30 shielded twisted cable (Electra 7301p)
PDIGR-AFS-262-112 | Distech | #REF! | white = signal, black = Common | 0-500Pa Air Switch | Filter Status | 1 pair 7/0.30 shielded twisted cable (Electra 7301p)
PDIGR-WP-D-111-LCD | Distech | #REF! | red = 24VAC, white = 0-10VDC, black = Common | 0-100, 200, 500 & 1000kPa Wet Pressure with LCD | ChW/HW Loop Pressure | 3 core 7/0.30 shielded twisted cable (Electra 7303C)
PDIGR-CDD1A4000-T24 | Distech | #REF! | red = 24VAC, white = 0-10VDC, black = Common & white = signal, black = common | Wall Mount CO2 & Temp | Space CO2 & Temp | 3 core 7/0.30 shielded twisted cable (Electra 7303C) & 1 pair 7/030 shielded twisted cable (Electra 7301p)
PDIGR-LP2B06S | Distech | #REF! | red = 24VAC, white = 0-10VDC, black = Common | 0-500. 1000Pa Air Pressure Sensor with LCD and static pickup | Static Pressure | 3 core 7/0.30 shielded twisted cable (Electra 7303C)
PDIGR-TE200BE24D2 | Distech | #REF! | white = signal, black = Common | Duct Mount, 200mm Sensor | Duct Temp | 1 pair 7/0.30 shielded twisted cable (Electra 7301p)
PDIGR-IE200BE24D2 | Distech | #REF! | white = signal, black = Common | Duct Mount, 200mm Sensor | Duct Temp | 1 pair 7/0.30 shielded twisted cable (Electra 7301p)
PDITE-SENSORX0 | Distech | #REF! | white = signal, black = Common | Temperature |  | 1 pair 7/0.30 shielded twisted cable (Electra 7301p)
PDIGR-TE200BE24B2 + well | Distech | #REF! | white = signal, black = Common | Temperature |  | 2 pair 7/0.30 shielded twisted cable (Electra 7301p)
E1210 | MOXA | #REF!
PDIGR-TE200FDB24A | Distech | #REF! | white = signal, black = Common | Duct Mount averaging 1.8 m | Duct Temp Averaging | 1 pair 7/0.30 shielded twisted cable (Electra 7301p)
PDIGR-TE200CE24C2E + well | Distech | #REF! | white = signal, black = Common | Immersion Temperature |  | 2 pair 7/0.30 shielded twisted cable (Electra 7301p)
Software Point |  | #REF! | - | - | - | -
Limit of dropdown list |  | #REF!
ECB103 |  | #REF!
ECB203 |  | #REF!
ECB300 |  | #REF!
ECB400 |  | #REF!
ECB600 |  | #REF!
ECX420 |  | #REF!
ECX400 |  | #REF!
VAVO |  | #REF!
VAVS |  | #REF!
VAV |  | #REF!
ECB600 + ECX400 |  | #REF!
Modulating Actuator Terminal | CO2 Sensor | #REF! |  | 1 | Damper Control | Shielded twisted 3 Pair (Electra 7303P) |  |  | RA Duct Work | 1
VSD Terminal | VOC Sensor | #REF! |  | 1 | Fan Speed Control | 1 pair 7/0.30 shielded twisted cable (Electra 7301p) |  |  | RA Duct Work
- | - | #REF! | - | - | - | -
UPS Terminals |  | #REF!
Fire Relay |  | #REF!
#REF!
SSA61 |  | #REF!
SSD61 |  | #REF!
SQD65 |  | #REF!
SAX61 |  | #REF!
STA63 |  | #REF!
Limit of dropdown list
Immersion
Temp with PB
PC
SSR
Door Reed Switch
Flow Meters
VSDs
Smoke Dampers