## Revision
Date | Controller | Revision | Changes | By
2014-08-13 |  | A | Initial | MJS
2015-02-08 |  | B | Review | MJS
2015-03-05 |  | C | Engineering Review | VZ
2015-03-23 |  | D | Engineering Review

## Points
Controlworks Pty Ltd
| Lismore Hospital | DATE | 5 | Nov | 2015 | [12 empty] | REV 3.1 |  |  | 2015-11-05
Project Number: PQ770
| Point Name | DI | DO | AI | AO | HLI | Prog | Alarms |  |  | Graphics |  | History Data |  | Point ID | System Location | System | Point | Controller | I/O | Location | Hardware | Qty
Comms Room 3002
Level-3 | FCU-L3-01 | DI | DO | AI | AO | HLI | Prog | Condition | Timing | Priority | Graphic Name | Functionality | Frequency |  |  |  |  | MAC 3 |  |  |  | ECB203 | 1
Level-3 | Schedule | [5 empty] | 1 |  |  |  | FCU | Display & Override | 10 Min or > 5% COV |  | FCU-L3-01-SW01 | Level-3 | FCU-L3-01 | Schedule | FCU-L3-01 | SW01 | Software | Software Point | 1
Level-3 | Fan Enable |  | 1 | [8 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L3-01-DO1 | Level-3 | FCU-L3-01 | Fan Enable | FCU-L3-01 | DO1 | MSSB | 24VAC Relay | 1
Level-3 | Fan Status | 1 | [5 empty] | Mismatch with enable | 60s | Critical |  | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L3-01-UI1 | Level-3 | FCU-L3-01 | Fan Status | FCU-L3-01 | UI1 | MSSB | CCS | 1
Level-3 | SA Temp |  |  | 1 | [7 empty] | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L3-01-UI2 | Level-3 | FCU-L3-01 | SA Temp | FCU-L3-01 | UI2 | SA Ductwork | PDIGR-TE200BE24B2 | 1
Level-3 | Space Temp |  |  | 1 |  |  |  | >or< Setpoint by 2°C | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L3-01-UI3 | Level-3 | FCU-L3-01 | Space Temp | FCU-L3-01 | UI3 | Space | PDITE-SENSORX0 | 1
Level-3 | Dirty Filter | 1 | [5 empty] | COS | 60s | Maint |  | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L3-01-UI4 | Level-3 | FCU-L3-01 | Dirty Filter | FCU-L3-01 | UI4 | Filter Box | AFS - 930.80222524 | 1
Level-3 | CHW Valve |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L3-01-UO6 | Level-3 | FCU-L3-01 | CHW Valve | FCU-L3-01 | UO6 | FCU | CHWV Actuator | 1
-
| Sub Total | 2 | 1 | 2 | 1 | 0 | 1
Lift Lobby and Corridor Areas 3C01
Level-3 | FCU-L3-02 | DI | DO | AI | AO | HLI | Prog | Condition | Timing | Priority | Graphic Name | Functionality | Frequency |  |  |  |  | MAC 4 |  |  |  | ECB203 | 1
Level-3 | Schedule | [5 empty] | 1 |  |  |  | FCU | Display & Override | 10 Min or > 5% COV |  | FCU-L3-02-SW01 | Level-3 | FCU-L3-02 | Schedule | FCU-L3-02 | SW01 | Software | Software Point | 1
Level-3 | Fan Enable |  | 1 | [8 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L3-02-DO1 | Level-3 | FCU-L3-02 | Fan Enable | FCU-L3-02 | DO1 | MSSB | 24VAC Relay | 1
Level-3 | OAF-L3-01 Fan Enable |  | 1 | [8 empty] | Display & Override | 10 Min or > 5% COV |  | OAF-L3-01-DO2 | Level-3 | OAF-L3-01 | OAF-L3-01 Fan Enable | OAF-L3-01 | DO2 | MSSB | 24VAC Relay | 1
Level-3 | Fan Status | 1 | [5 empty] | Mismatch with enable | 60s | Critical |  | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L3-02-UI1 | Level-3 | FCU-L3-02 | Fan Status | FCU-L3-02 | UI1 | MSSB | CCS | 1
Level-3 | SA Temp |  |  | 1 | [7 empty] | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L3-02-UI2 | Level-3 | FCU-L3-02 | SA Temp | FCU-L3-02 | UI2 | SA Ductwork | PDIGR-TE200BE24B2 | 1
Level-3 | RA Temp |  |  | 1 |  |  |  | >or< Setpoint by 2°C | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L3-02-UI3 | Level-3 | FCU-L3-02 | RA Temp | FCU-L3-02 | UI3 | RA Ductwork | PDIGR-TE200BE24B2 | 1
Level-3 | Dirty Filter | 1 | [5 empty] | Change of State | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L3-02-UI4 | Level-3 | FCU-L3-02 | Dirty Filter | FCU-L3-02 | UI4 | Filter Box | AFS - 930.80222524 | 1
Level-3 | OAF-L3-01 Status | 1 | [12 empty] | OAF-L3-01-UI5 | Level-3 | OAF-L3-01 | OAF-L3-01 Status | OAF-L3-01 | UI5 | MSSB | CCS | 1
Level-3 | Fire | 1 | [5 empty] | COS | 0s | Fire |  | Display / Red on Alarm | 10 Min or > 5% COV |  | L3 Fire Signal-UI5 | Level-3 | L3 Fire Signal | Fire | L3 Fire Signal | UI5 | MSSB | 24VAC Relay | 1
Level-3 | CHW Valve |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L3-02-UO6 | Level-3 | FCU-L3-02 | CHW Valve | FCU-L3-02 | UO6 | FCU | CHWV Actuator | 1
Level-3 | HW Valve |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L3-02-UO7 | Level-3 | FCU-L3-02 | HW Valve | FCU-L3-02 | UO7 | FCU | HHWV Actuator | 1
-
| Sub Total | 4 | 2 | 2 | 2 | 0 | 1
Lift Lobby and Corridor Areas 3C01
Level-3 | FCU-L3-03 | DI | DO | AI | AO | HLI | Prog | Condition | Timing | Priority | Graphic Name | Functionality | Frequency | [8 empty] | ECB203 | 1
Level-3 | Schedule | [5 empty] | 1 |  |  |  | FCU | Display & Override | 10 Min or > 5% COV |  | FCU-L3-03-SW01 | Level-3 | FCU-L3-03 | Schedule | FCU-L3-03 | SW01 | Software | Software Point | 1
Level-3 | Fan Enable |  | 1 | [8 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L3-03-DO1 | Level-3 | FCU-L3-03 | Fan Enable | FCU-L3-03 | DO1 | MSSB | 24VAC Relay | 1
Level-3 | Fan Status | 1 | [5 empty] | Mismatch with enable | 60s | Critical |  | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L3-03-UI1 | Level-3 | FCU-L3-03 | Fan Status | FCU-L3-03 | UI1 | MSSB | CCS | 1
Level-3 | SA Temp |  |  | 1 | [7 empty] | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L3-03-UI2 | Level-3 | FCU-L3-03 | SA Temp | FCU-L3-03 | UI2 | SA Ductwork | PDIGR-TE200BE24B2 | 1
Level-3 | RA Temp |  |  | 1 |  |  |  | >or< Setpoint by 2°C | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 11 Min or > 5% COV |  | FCU-L3-03-UI3 | Level-3 | FCU-L3-03 | RA Temp | FCU-L3-03 | UI3 | RA Ductwork | PDIGR-TE200BE24B2 | 1
Level-3 | Dirty Filter | 1 | [5 empty] | Change of State | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L3-03-UI4 | Level-3 | FCU-L3-03 | Dirty Filter | FCU-L3-03 | UI4 | Filter Box | AFS - 930.80222524 | 1
Level-3 | CHW Valve |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L3-03-UO6 | Level-3 | FCU-L3-03 | CHW Valve | FCU-L3-03 | UO6 | FCU | CHWV Actuator | 1
Level-3 | HW Valve |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L3-03-UO7 | Level-3 | FCU-L3-03 | HW Valve | FCU-L3-03 | UO7 | FCU | HHWV Actuator | 1
-
| Sub Total | 2 | 1 | 2 | 2 | 0 | 1
UPS Room 3E01
Level-3 | FCU-L3-04 | DI | DO | AI | AO | HLI | Prog | Condition | Timing | Priority | Graphic Name | Functionality | Frequency | [8 empty] | ECB203 | 1
Level-3 | Schedule | [5 empty] | 1 |  |  |  | FCU | Display & Override | 10 Min or > 5% COV |  | FCU-L3-04-SW01 | Level-3 | FCU-L3-04 | Schedule | FCU-L3-04 | SW01 | Software | Software Point | 1
Level-3 | Fan Enable |  | 1 | [8 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L3-04-DO1 | Level-3 | FCU-L3-04 | Fan Enable | FCU-L3-04 | DO1 | MSSB | 24VAC Relay | 1
Level-3 | Fan Status | 1 | [5 empty] | Mismatch with enable | 60s | Critical |  | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L3-04-UI1 | Level-3 | FCU-L3-04 | Fan Status | FCU-L3-04 | UI1 | MSSB | CCS | 1
Level-3 | SA Temp |  |  | 1 | [7 empty] | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L3-04-UI2 | Level-3 | FCU-L3-04 | SA Temp | FCU-L3-04 | UI2 | SA Ductwork | PDIGR-TE200BE24B2 | 1
Level-3 | RA Temp |  |  | 1 |  |  |  | >or< Setpoint by 2°C | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 11 Min or > 5% COV |  | FCU-L3-04-UI3 | Level-3 | FCU-L3-04 | RA Temp | FCU-L3-04 | UI3 | RA Ductwork | PDIGR-TE200BE24B2 | 1
Level-3 | Dirty Filter | 1 | [5 empty] | Change of State | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L3-04-UI4 | Level-3 | FCU-L3-04 | Dirty Filter | FCU-L3-04 | UI4 | Filter Box | AFS - 930.80222524 | 1
Level-3 | CHW Valve |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L3-04-UO6 | Level-3 | FCU-L3-04 | CHW Valve | FCU-L3-04 | UO6 | FCU | CHWV Actuator | 1
Level-3 | Spare | [10 empty] | Display & Override | 10 Min or > 5% COV | [6 empty] | UO7
Level-3 | Fan Speed |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L3-04-UO8 | Level-3 | FCU-L3-04 | Fan Speed | FCU-L3-04 | UO8 | FCU | Terminals | 1
| Sub Total | 2 | 1 | 2 | 2 | 0 | 1
UPS Room 3E01
Level-3 | FCU-L3-05 | DI | DO | AI | AO | HLI | Prog | Condition | Timing | Priority | Graphic Name | Functionality | Frequency | [8 empty] | ECB203 | 1
Level-3 | Schedule | [5 empty] | 1 |  |  |  | FCU | Display & Override | 10 Min or > 5% COV |  | FCU-L3-05-SW01 | Level-3 | FCU-L3-05 | Schedule | FCU-L3-05 | SW01 | Software | Software Point | 1
Level-3 | Fan Enable |  | 1 | [8 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L3-05-DO1 | Level-3 | FCU-L3-05 | Fan Enable | FCU-L3-05 | DO1 | MSSB | 24VAC Relay | 1
Level-3 | Fan Status | 1 | [5 empty] | Mismatch with enable | 60s | Critical |  | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L3-05-UI1 | Level-3 | FCU-L3-05 | Fan Status | FCU-L3-05 | UI1 | MSSB | CCS | 1
Level-3 | SA Temp |  |  | 1 | [7 empty] | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L3-05-UI2 | Level-3 | FCU-L3-05 | SA Temp | FCU-L3-05 | UI2 | SA Ductwork | PDIGR-TE200BE24B2 | 1
Level-3 | RA Temp |  |  | 1 |  |  |  | >or< Setpoint by 2°C | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 11 Min or > 5% COV |  | FCU-L3-05-UI3 | Level-3 | FCU-L3-05 | RA Temp | FCU-L3-05 | UI3 | RA Ductwork | PDIGR-TE200BE24B2 | 1
Level-3 | Dirty Filter | 1 | [5 empty] | Change of State | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L3-05-UI4 | Level-3 | FCU-L3-05 | Dirty Filter | FCU-L3-05 | UI4 | Filter Box | AFS - 930.80222524 | 1
Level-3 | GEF-L3-02 Status | 1 | [12 empty] | GEF-L3-02-UI5 | Level-3 | GEF-L3-02 | GEF-L3-02 Status | GEF-L3-02 | UI5 | EA Ductwork | AFS - 930.80222524 | 1
Level-3 | GEF-L3-03 Status | 1 | [12 empty] | GEF-L3-03-UI6 | Level-3 | GEF-L3-03 | GEF-L3-03 Status | GEF-L3-03 | UI6 | EA Ductwork | AFS - 930.80222524 | 1
Level-3 | CHW Valve |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L3-05-UO6 | Level-3 | FCU-L3-05 | CHW Valve | FCU-L3-05 | UO6 | FCU | CHWV Actuator | 1
Level-3 | Spare | [10 empty] | Display & Override | 10 Min or > 5% COV |  |  |  |  | Spare |  | UO7
Level-3 | Fan Speed |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L3-05-UO8 | Level-3 | FCU-L3-05 | Fan Speed | FCU-L3-05 | UO8 | FCU | Terminals | 1
| Sub Total | 4 | 1 | 2 | 2 | 0 | 1
Main Switch Room 3E02
Level-3 | FCU-L3-06 | DI | DO | AI | AO | HLI | Prog | Condition | Timing | Priority | Graphic Name | Functionality | Frequency | [8 empty] | ECB203 | 1
Level-3 | Schedule | [5 empty] | 1 |  |  |  | FCU | Display & Override | 10 Min or > 5% COV |  | FCU-L3-06-SW01 | Level-3 | FCU-L3-06 | Schedule | FCU-L3-06 | SW01 | Software | Software Point | 1
Level-3 | Fan Enable |  | 1 | [8 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L3-06-DO1 | Level-3 | FCU-L3-06 | Fan Enable | FCU-L3-06 | DO1 | MSSB | 24VAC Relay | 1
Level-3 | Fan Status | 1 | [5 empty] | Mismatch with enable | 60s | Critical |  | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L3-06-UI1 | Level-3 | FCU-L3-06 | Fan Status | FCU-L3-06 | UI1 | MSSB | CCS | 1
Level-3 | SA Temp |  |  | 1 | [7 empty] | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L3-06-UI2 | Level-3 | FCU-L3-06 | SA Temp | FCU-L3-06 | UI2 | SA Ductwork | PDIGR-TE200BE24B2 | 1
Level-3 | RA Temp |  |  | 1 |  |  |  | >or< Setpoint by 2°C | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 11 Min or > 5% COV |  | FCU-L3-06-UI3 | Level-3 | FCU-L3-06 | RA Temp | FCU-L3-06 | UI3 | RA Ductwork | PDIGR-TE200BE24B2 | 1
Level-3 | Dirty Filter | 1 | [5 empty] | Change of State | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L3-06-UI4 | Level-3 | FCU-L3-06 | Dirty Filter | FCU-L3-06 | UI4 | Filter Box | AFS - 930.80222524 | 1
Level-3 | CHW Valve |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L3-06-UO6 | Level-3 | FCU-L3-06 | CHW Valve | FCU-L3-06 | UO6 | FCU | CHWV Actuator | 1
Level-3 | Spare | [10 empty] | Display & Override | 10 Min or > 5% COV |  |  |  |  | Spare |  | UO7
Level-3 | Fan Speed |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L3-06-UO8 | Level-3 | FCU-L3-06 | Fan Speed | FCU-L3-06 | UO8 | FCU | Terminals | 1
| Sub Total | 2 | 1 | 2 | 2 | 0 | 1
Level 3- Plant Areas 3H01/3H02
| GEF-L3-01 | DI | DO | AI | AO | HLI | Prog | Condition | Timing | Priority | Graphic Name | Functionality | Frequency | [8 empty] | VSD-GEF-L3-01
Vent Fans | Enable |  |  |  |  | 1 |  |  |  |  | GEF-L3-01 | Display & Override | COV |  | GEF-L3-01-SW01 | Level-3 | GEF-L3-01 | Enable | GEF-L3-01 | SW01 | Level-3 | -
Vent Fans | Status |  |  |  |  | 1 |  | Mismatch with enable | 60s | Critical |  | Display / Red on Alarm | COV |  | GEF-L3-01-SW02 | Level-3 | GEF-L3-01 | Status | GEF-L3-01 | SW02 | Level-3 | -
Vent Fans | VSD Fault |  |  |  |  | 1 |  | Change Of State | 60s | Critical |  | Display / Red on Alarm | COV |  | GEF-L3-01-SW03 | Level-3 | GEF-L3-01 | VSD Fault | GEF-L3-01 | SW03 | Level-3 | -
Vent Fans | VSD Speed Control |  |  |  |  | 1 | [5 empty] | Display Only | 60s |  | GEF-L3-01-SW04 | Level-3 | GEF-L3-01 | VSD Speed Control | GEF-L3-01 | SW04 | Level-3 | -
| Sub Total | 0 | 0 | 0 | 0 | 4 | 0
Level 3 – UPS Room
| GEF-L3-02 | DI | DO | AI | AO | HLI | Prog | Condition | Timing | Priority | Graphic Name | Functionality | Frequency | [8 empty] | VSD-GEF-L3-02
Vent Fans | Enable |  |  |  |  | 1 |  |  |  |  | GEF-L3-02 | Display & Override | COV |  | GEF-L3-02-SW01 | Level-3 | GEF-L3-02 | Enable | GEF-L3-02 | SW01 | Level-3 | -
Vent Fans | Status |  |  |  |  | 1 |  | Mismatch with enable | 60s | Critical |  | Display / Red on Alarm | COV |  | GEF-L3-02-SW02 | Level-3 | GEF-L3-02 | Status | GEF-L3-02 | SW02 | Level-3 | -
Vent Fans | VSD Fault |  |  |  |  | 1 |  | Change Of State | 60s | Critical |  | Display / Red on Alarm | COV |  | GEF-L3-02-SW03 | Level-3 | GEF-L3-02 | VSD Fault | GEF-L3-02 | SW03 | Level-3 | -
Vent Fans | VSD Speed Control |  |  |  |  | 1 | [5 empty] | Display Only | 60s |  | GEF-L3-02-SW04 | Level-3 | GEF-L3-02 | VSD Speed Control | GEF-L3-02 | SW04 | Level-3 | -
| Sub Total | 0 | 0 | 0 | 0 | 4 | 0
Level 3 – UPS Room
| GEF-L3-03 | DI | DO | AI | AO | HLI | Prog | Condition | Timing | Priority | Graphic Name | Functionality | Frequency | [8 empty] | VSD-GEF-L3-03
Vent Fans | Enable |  |  |  |  | 1 |  |  |  |  | GEF-L3-03 | Display & Override | COV |  | GEF-L3-03-SW01 | Level-3 | GEF-L3-03 | Enable | GEF-L3-03 | SW01 | Level-3 | -
Vent Fans | Status |  |  |  |  | 1 |  | Mismatch with enable | 60s | Critical |  | Display / Red on Alarm | COV |  | GEF-L3-03-SW02 | Level-3 | GEF-L3-03 | Status | GEF-L3-03 | SW02 | Level-3 | -
Vent Fans | VSD Fault |  |  |  |  | 1 |  | Change Of State | 60s | Critical |  | Display / Red on Alarm | COV |  | GEF-L3-03-SW03 | Level-3 | GEF-L3-03 | VSD Fault | GEF-L3-03 | SW03 | Level-3 | -
Vent Fans | VSD Speed Control |  |  |  |  | 1 | [5 empty] | Display Only | 60s |  | GEF-L3-03-SW04 | Level-3 | GEF-L3-03 | VSD Speed Control | GEF-L3-03 | SW04 | Level-3 | -
| Sub Total | 0 | 0 | 0 | 0 | 4 | 0
| MSB MISC | DI | DO | AI | AO | HLI | Prog | Condition | Timing | Priority | Graphic Name | Functionality | Frequency |  | ECB600 |  |  | MSB Room |  |  |  | ECB600 | 1
Level-3 | Gas Meter 1 Pulse | 1 | [9 empty] | Display only | COV |  | MSB MISC-UI1 | Site Boundaries | MSB MISC | Gas Meter 1 Pulse | MSB MISC | UI1 | Level-3 | Terminals | 1
Level-3 | Gas Meter 2 Pulse | 1 | [9 empty] | Display only | COV |  | MSB MISC-UI2 | Site Boundaries | MSB MISC | Gas Meter 2 Pulse | MSB MISC | UI2 | Level-3 | Terminals | 1
Level-3 | Gas Meter 3 Pulse | 1 | [9 empty] | Display only | COV |  | MSB MISC-UI3 | Site Boundaries | MSB MISC | Gas Meter 3 Pulse | MSB MISC | UI3 | Level-3 | Terminals | 1
Level-3 | UV Steriliser 1 Hours Run Counter | 1 | [9 empty] | Display only | COV |  | MSB MISC-UI4 | Site Boundaries | MSB MISC | UV Steriliser 1 Hours Run Counter | MSB MISC | UI4 | Level-3 | Terminals | 1
Level-3 | IO-DIM6-1 |  |  | 1 | [7 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | IO-DIM6-1 |  | UI5 |  | IO-DIM6 | 1
Level-3 | CB F1-1 N10 Open | 1 | [9 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | CB F1-1 N10 Open | MSB MISC |  |  | Terminals
Level-3 | CB F1-1 N10 Close | 1 | [9 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | CB F1-1 N10 Close | MSB MISC
Level-3 | CB F1-1 N10 Trip | 1 | [9 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | CB F1-1 N10 Trip | MSB MISC
Level-3 | CB F1-9 N2 Open | 1 | [9 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | CB F1-9 N2 Open | MSB MISC
Level-3 | CB F1-9 N2 Close | 1 | [13 empty] | L3 MSB |  | CB F1-9 N2 Close | MSB MISC
Level-3 | CB F1-9 N2 Trip | 1 | [13 empty] | L3 MSB |  | CB F1-9 N2 Trip | MSB MISC
Level-3 | IO-DIM6-2 |  |  | 1 | [7 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | IO-DIM6-2 |  | UI6 |  | IO-DIM6 | 1
Level-3 | CB F1-11 N1 Open | 1 | [9 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | CB F1-11 N1 Open | MSB MISC |  |  | Terminals
Level-3 | CB F1-11 N1 Close | 1 | [9 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | CB F1-11 N1 Close | MSB MISC
Level-3 | CB F1-11 N1 Trip | 1 | [9 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | CB F1-11 N1 Trip | MSB MISC
Level-3 | CB F1-15 N7 Open | 1 | [9 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | CB F1-15 N7 Open | MSB MISC
Level-3 | CB F1-15 N7 Close | 1 | [13 empty] | L3 MSB |  | CB F1-15 N7 Close | MSB MISC
Level-3 | CB F1-15 N7 Trip | 1 | [13 empty] | L3 MSB |  | CB F1-15 N7 Trip | MSB MISC
Level-3 | IO-DIM6-3 |  |  | 1 | [7 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | IO-DIM6-3 |  | UI7 |  | IO-DIM6 | 1
Level-3 | CB F2-1 N3 Open | 1 | [9 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | CB F2-1 N3 Open | MSB MISC |  |  | Terminals
Level-3 | CB F2-1 N3 Close | 1 | [9 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | CB F2-1 N3 Close | MSB MISC
Level-3 | CB F2-1 N3 Trip | 1 | [9 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | CB F2-1 N3 Trip | MSB MISC
Level-3 | CB F2-3 N4 Open | 1 | [9 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | CB F2-3 N4 Open | MSB MISC
Level-3 | CB F2-3 N4 Close | 1 | [13 empty] | L3 MSB |  | CB F2-3 N4 Close | MSB MISC
Level-3 | CB F2-3 N4 Trip | 1 | [13 empty] | L3 MSB |  | CB F2-3 N4 Trip | MSB MISC
Level-3 | IO-DIM6-4 |  |  | 1 | [7 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | IO-DIM6-4 |  | UI8 |  | IO-DIM6 | 1
Level-3 | CB F2-5 N5 Open | 1 | [9 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | CB F2-5 N5 Open | MSB MISC |  |  | Terminals
Level-3 | CB F2-5 N5 Close | 1 | [9 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | CB F2-5 N5 Close | MSB MISC
Level-3 | CB F2-5 N5 Trip | 1 | [9 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | CB F2-5 N5 Trip | MSB MISC
Level-3 | CB F2-7 N6 Open | 1 | [9 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | CB F2-7 N6 Open | MSB MISC
Level-3 | CB F2-7 N6 Close | 1 | [13 empty] | L3 MSB |  | CB F2-7 N6 Close | MSB MISC
Level-3 | CB F2-7 N6 Trip | 1 | [13 empty] | L3 MSB |  | CB F2-7 N6 Trip | MSB MISC
Level-3 | IO-DIM6-5 |  |  | 1 | [7 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | IO-DIM6-5 |  | UI9 |  | IO-DIM6 | 1
Level-3 | CB F2-9 Spare 160A Open | 1 | [9 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | CB F2-9 Spare 160A Open | MSB MISC |  |  | Terminals
Level-3 | CB F2-9 Spare 160A Close | 1 | [9 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | CB F2-9 Spare 160A Close | MSB MISC
Level-3 | CB F2-9 Spare 160A Trip | 1 | [9 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | CB F2-9 Spare 160A Trip | MSB MISC
Level-3 | CB F2-11 Spare 400A Open | 1 | [9 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | CB F2-11 Spare 400A Open | MSB MISC
Level-3 | CB F2-11 Spare 400A Close | 1 | [13 empty] | L3 MSB |  | CB F2-11 Spare 400A Close | MSB MISC
Level-3 | CB F2-11 Spare 400A Trip | 1 | [13 empty] | L3 MSB |  | CB F2-11 Spare 400A Trip | MSB MISC
Level-3 | IO-DIM6-6 |  |  | 1 | [7 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | IO-DIM6-6 |  | UI10 |  | IO-DIM6 | 1
Level-3 | CB F3-1 Spare 160A Open | 1 | [9 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | CB F3-1 Spare 160A Open | MSB MISC |  |  | Terminals
Level-3 | CB F3-1 Spare 160A Close | 1 | [9 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | CB F3-1 Spare 160A Close | MSB MISC
Level-3 | CB F3-1 Spare 160A Trip | 1 | [9 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | CB F3-1 Spare 160A Trip | MSB MISC
Level-3 | CB F3-2 Spare 160A Open | 1 | [9 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | CB F3-2 Spare 160A Open | MSB MISC
Level-3 | CB F3-2 Spare 160A Close | 1 | [13 empty] | L3 MSB |  | CB F3-2 Spare 160A Close | MSB MISC
Level-3 | CB F3-2 Spare 160A Trip | 1 | [13 empty] | L3 MSB |  | CB F3-2 Spare 160A Trip | MSB MISC
Level-3 | IO-DIM6-7 |  |  | 1 | [7 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | IO-DIM6-7 |  | UI11 |  | IO-DIM6 | 1
Level-3 | CB F3-5 Spare 250A Open | 1 | [9 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | CB F3-5 Spare 250A Open | MSB MISC |  |  | Terminals
Level-3 | CB F3-5 Spare 250A Close | 1 | [9 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | CB F3-5 Spare 250A Close | MSB MISC
Level-3 | CB F3-5 Spare 250A Trip | 1 | [9 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | CB F3-5 Spare 250A Trip | MSB MISC
Level-3 | CB F3-7 Spare 250A Open | 1 | [9 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | CB F3-7 Spare 250A Open | MSB MISC
Level-3 | CB F3-7 Spare 250A Close | 1 | [13 empty] | L3 MSB |  | CB F3-7 Spare 250A Close | MSB MISC
Level-3 | CB F3-7 Spare 250A Trip | 1 | [13 empty] | L3 MSB |  | CB F3-7 Spare 250A Trip | MSB MISC
Level-3 | IO-DIM6-8 |  |  | 1 | [7 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | IO-DIM6-8 |  | UI12 |  | IO-DIM6 | 1
Level-3 | CB F3-9 Spare 250A Open | 1 | [9 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | CB F3-9 Spare 250A Open | MSB MISC |  |  | Terminals
Level-3 | CB F3-9 Spare 250A Close | 1 | [9 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | CB F3-9 Spare 250A Close | MSB MISC
Level-3 | CB F3-9 Spare 250A Trip | 1 | [9 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | CB F3-9 Spare 250A Trip | MSB MISC
Level-3 | CB F3-11 Spare 400A Open | 1 | [9 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | CB F3-11 Spare 400A Open | MSB MISC
Level-3 | CB F3-11 Spare 400A Close | 1 | [13 empty] | L3 MSB |  | CB F3-11 Spare 400A Close | MSB MISC
Level-3 | CB F3-11 Spare 400A Trip | 1 | [13 empty] | L3 MSB |  | CB F3-11 Spare 400A Trip | MSB MISC
Level-3 | IO-DIM6-9 |  |  | 1 | [7 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | IO-DIM6-9 |  | UI13 |  | IO-DIM6 | 1
Level-3 | CB F3-14 Spare 630A Open | 1 | [9 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | CB F3-14 Spare 630A Open | MSB MISC |  |  | Terminals
Level-3 | CB F3-14 Spare 630A Close | 1 | [9 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | CB F3-14 Spare 630A Close | MSB MISC
Level-3 | CB F3-14 Spare 630A Trip | 1 | [9 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | CB F3-14 Spare 630A Trip | MSB MISC
Level-3 | CB F8-1 Spare 160A Open | 1 | [9 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | CB F8-1 Spare 160A Open | MSB MISC
Level-3 | CB F8-1 Spare 160A Close | 1 | [13 empty] | L3 MSB |  | CB F8-1 Spare 160A Close | MSB MISC
Level-3 | CB F8-1 Spare 160A Trip | 1 | [13 empty] | L3 MSB |  | CB F8-1 Spare 160A Trip | MSB MISC
Level-3 | IO-DIM6-10 |  |  | 1 | [7 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | IO-DIM6-10 |  | UI14 |  | IO-DIM6 | 1
Level-3 | CB F8-3 Spare 160A Open | 1 | [9 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | CB F8-3 Spare 160A Open | MSB MISC |  |  | Terminals
Level-3 | CB F8-3 Spare 160A Close | 1 | [9 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | CB F8-3 Spare 160A Close | MSB MISC
Level-3 | CB F8-3 Spare 160A Trip | 1 | [9 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | CB F8-3 Spare 160A Trip | MSB MISC
Level-3 | CB F8-7 Spare 160A Open | 1 | [9 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | CB F8-7 Spare 160A Open | MSB MISC
Level-3 | CB F8-7 Spare 160A Close | 1 | [13 empty] | L3 MSB |  | CB F8-7 Spare 160A Close | MSB MISC
Level-3 | CB F8-7 Spare 160A Trip | 1 | [13 empty] | L3 MSB |  | CB F8-7 Spare 160A Trip | MSB MISC
Level-3 | IO-DIM6-11 |  |  | 1 | [7 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | IO-DIM6-11 |  | UI15 |  | IO-DIM6 | 1
Level-3 | CB F8-9 E9 Open | 1 | [9 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | CB F8-9 E9 Open | MSB MISC |  |  | Terminals
Level-3 | CB F8-9 E9 Close | 1 | [9 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | CB F8-9 E9 Close | MSB MISC
Level-3 | CB F8-9 E9 Trip | 1 | [9 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | CB F8-9 E9 Trip | MSB MISC
Level-3 | CB F8-11 E8 Open | 1 | [9 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | CB F8-11 E8 Open | MSB MISC
Level-3 | CB F8-11 E8 Close | 1 | [13 empty] | L3 MSB |  | CB F8-11 E8 Close | MSB MISC
Level-3 | CB F8-11 E8 Trip | 1 | [13 empty] | L3 MSB |  | CB F8-11 E8 Trip | MSB MISC
Level-3 | IO-DIM6-12 |  |  | 1 | [7 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | IO-DIM6-12 |  | UI16 |  | IO-DIM6 | 1
Level-3 | CB F8-13 E25 Open | 1 | [9 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | CB F8-13 E25 Open | MSB MISC |  |  | Terminals
Level-3 | CB F8-13 E25 Close | 1 | [9 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | CB F8-13 E25 Close | MSB MISC
Level-3 | CB F8-13 E25 Trip | 1 | [9 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | CB F8-13 E25 Trip | MSB MISC
Level-3 | CB F11-1 Spare 250A Open | 1 | [9 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | CB F11-1 Spare 250A Open | MSB MISC
Level-3 | CB F11-1 Spare 250A Close | 1 | [13 empty] | L3 MSB |  | CB F11-1 Spare 250A Close | MSB MISC
Level-3 | CB F11-1 Spare 250A Trip | 1 | [13 empty] | L3 MSB |  | CB F11-1 Spare 250A Trip | MSB MISC
| Sub Total | 76 | 0 | 12 | 0 | 0 | 0
| MSB MISC ECX420-1 | DI | DO | AI | AO | HLI | Prog | Condition | Timing | Priority | Graphic Name | Functionality | Frequency |  |  |  |  | ECB600 Subnet |  |  |  | ECX420 | 1
Level-3 | IO-DIM6-13 |  |  | 1 | [7 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | IO-DIM6-13 | MSB MISC ECX420-1 | UI1 |  | IO-DIM6 | 1
Level-3 | CB F11-3 Spare 250A Open | 1 | [9 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | CB F11-3 Spare 250A Open | MSB MISC ECX420-1 |  |  | Terminals
Level-3 | CB F11-3 Spare 250A Close | 1 | [9 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | CB F11-3 Spare 250A Close | MSB MISC ECX420-1
Level-3 | CB F11-3 Spare 250A Trip | 1 | [9 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | CB F11-3 Spare 250A Trip | MSB MISC ECX420-1
Level-3 | CB F11-5 Spare 250A Open | 1 | [9 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | CB F11-5 Spare 250A Open | MSB MISC ECX420-1
Level-3 | CB F11-5 Spare 250A Close | 1 | [13 empty] | L3 MSB |  | CB F11-5 Spare 250A Close | MSB MISC ECX420-1
Level-3 | CB F11-5 Spare 250A Trip | 1 | [13 empty] | L3 MSB |  | CB F11-5 Spare 250A Trip | MSB MISC ECX420-1
Level-3 | IO-DIM6-14 |  |  | 1 | [7 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | IO-DIM6-14 |  | UI2 |  | IO-DIM6 | 1
Level-3 | CB F11-7 E24 Open | 1 | [9 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | CB F11-7 E24 Open | MSB MISC ECX420-1 |  |  | Terminals
Level-3 | CB F11-7 E24 Close | 1 | [9 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | CB F11-7 E24 Close | MSB MISC ECX420-1
Level-3 | CB F11-7 E24 Trip | 1 | [9 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | CB F11-7 E24 Trip | MSB MISC ECX420-1
Level-3 | CB F11-9 E23 Open | 1 | [9 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | CB F11-9 E23 Open | MSB MISC ECX420-1
Level-3 | CB F11-9 E23 Close | 1 | [13 empty] | L3 MSB |  | CB F11-9 E23 Close | MSB MISC ECX420-1
Level-3 | CB F11-9 E23 Trip | 1 | [13 empty] | L3 MSB |  | CB F11-9 E23 Trip | MSB MISC ECX420-1
Level-3 | IO-DIM6-15 |  |  | 1 | [7 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | IO-DIM6-15 |  | UI3 |  | IO-DIM6 | 1
Level-3 | CB F11-11 E13 Open | 1 | [9 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | CB F11-11 E13 Open | MSB MISC ECX420-1 |  |  | Terminals
Level-3 | CB F11-11 E13 Close | 1 | [9 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | CB F11-11 E13 Close | MSB MISC ECX420-1
Level-3 | CB F11-11 E13 Trip | 1 | [9 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | CB F11-11 E13 Trip | MSB MISC ECX420-1
Level-3 | CB F11-14 Spare 630A Open | 1 | [9 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | CB F11-14 Spare 630A Open | MSB MISC ECX420-1
Level-3 | CB F11-14 Spare 630A Close | 1 | [13 empty] | L3 MSB |  | CB F11-14 Spare 630A Close | MSB MISC ECX420-1
Level-3 | CB F11-14 Spare 630A Trip | 1 | [13 empty] | L3 MSB |  | CB F11-14 Spare 630A Trip | MSB MISC ECX420-1
Level-3 | IO-DIM6-16 |  |  | 1 | [7 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | IO-DIM6-16 |  | UI4 |  | IO-DIM6 | 1
Level-3 | CB F12-5 E17 Open | 1 | [9 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | CB F12-5 E17 Open | MSB MISC ECX420-1 |  |  | Terminals
Level-3 | CB F12-5 E17 Close | 1 | [9 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | CB F12-5 E17 Close | MSB MISC ECX420-1
Level-3 | CB F12-5 E17 Trip | 1 | [9 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | CB F12-5 E17 Trip | MSB MISC ECX420-1
Level-3 | CB F12-7 E16 Open | 1 | [9 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | CB F12-7 E16 Open | MSB MISC ECX420-1
Level-3 | CB F12-7 E16 Close | 1 | [13 empty] | L3 MSB |  | CB F12-7 E16 Close | MSB MISC ECX420-1
Level-3 | CB F12-7 E16 Trip | 1 | [13 empty] | L3 MSB |  | CB F12-7 E16 Trip | MSB MISC ECX420-1
Level-3 | IO-DIM6-17 |  |  | 1 | [7 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | IO-DIM6-17 |  | UI5 |  | IO-DIM6 | 1
Level-3 | CB F12-9 E15 Open | 1 | [9 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | CB F12-9 E15 Open | MSB MISC ECX420-1 |  |  | Terminals
Level-3 | CB F12-9 E15 Close | 1 | [9 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | CB F12-9 E15 Close | MSB MISC ECX420-1
Level-3 | CB F12-9 E15 Trip | 1 | [9 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | CB F12-9 E15 Trip | MSB MISC ECX420-1
Level-3 | CB F12-11 Spare 400A Open | 1 | [9 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | CB F12-11 Spare 400A Open | MSB MISC ECX420-1
Level-3 | CB F12-11 Spare 400A Close | 1 | [13 empty] | L3 MSB |  | CB F12-11 Spare 400A Close | MSB MISC ECX420-1
Level-3 | CB F12-11 Spare 400A Trip | 1 | [13 empty] | L3 MSB |  | CB F12-11 Spare 400A Trip | MSB MISC ECX420-1
Level-3 | IO-DIM6-18 |  |  | 1 | [7 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | IO-DIM6-18 |  | UI6 |  | IO-DIM6 | 1
Level-3 | CB F12-14 Spare 630A Open | 1 | [9 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | CB F12-14 Spare 630A Open | MSB MISC ECX420-1 |  |  | Terminals
Level-3 | CB F12-14 Spare 630A Close | 1 | [9 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | CB F12-14 Spare 630A Close | MSB MISC ECX420-1
Level-3 | CB F12-14 Spare 630A Trip | 1 | [9 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | CB F12-14 Spare 630A Trip | MSB MISC ECX420-1
Level-3 | CB F13-1 Spare 160A Open | 1 | [9 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | CB F13-1 Spare 160A Open | MSB MISC ECX420-1
Level-3 | CB F13-1 Spare 160A Close | 1 | [13 empty] | L3 MSB |  | CB F13-1 Spare 160A Close | MSB MISC ECX420-1
Level-3 | CB F13-1 Spare 160A Trip | 1 | [13 empty] | L3 MSB |  | CB F13-1 Spare 160A Trip | MSB MISC ECX420-1
Level-3 | IO-DIM6-19 |  |  | 1 | [7 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | IO-DIM6-19 |  | UI7 |  | IO-DIM6 | 1
Level-3 | CB F13-3 Spare 160A Open | 1 | [9 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | CB F13-3 Spare 160A Open | MSB MISC ECX420-1 |  |  | Terminals
Level-3 | CB F13-3 Spare 160A Close | 1 | [9 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | CB F13-3 Spare 160A Close | MSB MISC ECX420-1
Level-3 | CB F13-3 Spare 160A Trip | 1 | [9 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | CB F13-3 Spare 160A Trip | MSB MISC ECX420-1
Level-3 | CB F13-5 Spare 160A Open | 1 | [9 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | CB F13-5 Spare 160A Open | MSB MISC ECX420-1
Level-3 | CB F13-5 Spare 160A Close | 1 | [13 empty] | L3 MSB |  | CB F13-5 Spare 160A Close | MSB MISC ECX420-1
Level-3 | CB F13-5 Spare 160A Trip | 1 | [13 empty] | L3 MSB |  | CB F13-5 Spare 160A Trip | MSB MISC ECX420-1
Level-3 | IO-DIM6-20 |  |  | 1 | [7 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | IO-DIM6-20 |  | UI8 |  | IO-DIM6 | 1
Level-3 | CB F13-7 E14 Open | 1 | [9 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | CB F13-7 E14 Open | MSB MISC ECX420-1 |  |  | Terminals | 1
Level-3 | CB F13-7 E14 Close | 1 | [9 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | CB F13-7 E14 Close | MSB MISC ECX420-1
Level-3 | CB F13-7 E14 Trip | 1 | [9 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | CB F13-7 E14 Trip | MSB MISC ECX420-1
Level-3 | CB F13-9 Spare 160A Open | 1 | [9 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | CB F13-9 Spare 160A Open | MSB MISC ECX420-1
Level-3 | CB F13-9 Spare 160A Close | 1 | [13 empty] | L3 MSB |  | CB F13-9 Spare 160A Close | MSB MISC ECX420-1
Level-3 | CB F13-9 Spare 160A Trip | 1 | [13 empty] | L3 MSB |  | CB F13-9 Spare 160A Trip | MSB MISC ECX420-1
Level-3 | IO-DIM6-21 |  |  | 1 | [7 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | IO-DIM6-21 |  | UI9 |  | IO-DIM6 | 1
Level-3 | CB F13-11 E22 Open | 1 | [9 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | CB F13-11 E22 Open | MSB MISC ECX420-1 |  |  | Terminals
Level-3 | CB F13-11 E22 Close | 1 | [9 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | CB F13-11 E22 Close | MSB MISC ECX420-1
Level-3 | CB F13-11 E22 Trip | 1 | [9 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | CB F13-11 E22 Trip | MSB MISC ECX420-1
Level-3 | CB F14-1 E21 Open | 1 | [9 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | CB F14-1 E21 Open | MSB MISC ECX420-1
Level-3 | CB F14-1 E21 Close | 1 | [13 empty] | L3 MSB |  | CB F14-1 E21 Close | MSB MISC ECX420-1
Level-3 | CB F14-1 E21 Trip | 1 | [13 empty] | L3 MSB |  | CB F14-1 E21 Trip | MSB MISC ECX420-1
Level-3 | IO-DIM6-22 |  |  | 1 | [7 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | IO-DIM6-22 |  | UI10 |  | IO-DIM6 | 1
Level-3 | CB F14-5 E12 Open | 1 | [9 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | CB F14-5 E12 Open | MSB MISC ECX420-1 |  |  | Terminals
Level-3 | CB F14-5 E12 Close | 1 | [9 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | CB F14-5 E12 Close | MSB MISC ECX420-1
Level-3 | CB F14-5 E12 Trip | 1 | [9 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | CB F14-5 E12 Trip | MSB MISC ECX420-1
Level-3 | CB F14-7 E11 Open | 1 | [9 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | CB F14-7 E11 Open | MSB MISC ECX420-1
Level-3 | CB F14-7 E11 Close | 1 | [13 empty] | L3 MSB |  | CB F14-7 E11 Close | MSB MISC ECX420-1
Level-3 | CB F14-7 E11 Trip | 1 | [13 empty] | L3 MSB |  | CB F14-7 E11 Trip | MSB MISC ECX420-1
Level-3 | IO-DIM6-23 |  |  | 1 | [7 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | IO-DIM6-23 |  | UI11 |  | IO-DIM6 | 1
Level-3 | CB F14-9 Spare 400A Open | 1 | [9 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | CB F14-9 Spare 400A Open | MSB MISC ECX420-1 |  |  | Terminals
Level-3 | CB F14-9 Spare 400A Close | 1 | [9 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | CB F14-9 Spare 400A Close | MSB MISC ECX420-1
Level-3 | CB F14-9 Spare 400A Trip | 1 | [9 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | CB F14-9 Spare 400A Trip | MSB MISC ECX420-1
Level-3 | CB F14-12 Spare 400A Open | 1 | [9 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | CB F14-12 Spare 400A Open | MSB MISC ECX420-1
Level-3 | CB F14-12 Spare 400A Close | 1 | [13 empty] | L3 MSB |  | CB F14-12 Spare 400A Close | MSB MISC ECX420-1
Level-3 | CB F14-12 Spare 400A Trip | 1 | [13 empty] | L3 MSB |  | CB F14-12 Spare 400A Trip | MSB MISC ECX420-1
Level-3 | IO-DIM6-24 |  |  | 1 | [7 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | IO-DIM6-24 |  | UI12 |  | IO-DIM6 | 1
Level-3 | CB F14-15 E10 Open | 1 | [9 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | CB F14-15 E10 Open | MSB MISC ECX420-1
Level-3 | CB F14-15 E10 Close | 1 | [13 empty] | L3 MSB |  | CB F14-15 E10 Close | MSB MISC ECX420-1
Level-3 | CB F14-15 E10 Trip | 1 | [13 empty] | L3 MSB |  | CB F14-15 E10 Trip | MSB MISC ECX420-1
Level-3 | Surge Diverter (Red) Fault | 1 | [13 empty] | L3 MSB |  | Surge Diverter (Red) Fault | MSB MISC ECX420-1
Level-3 | Surge Diverter (White) Fault | 1 | [13 empty] | L3 MSB |  | Surge Diverter (White) Fault | MSB MISC ECX420-1
Level-3 | Surge Diverter (Blue) Fault | 1 | [13 empty] | L3 MSB |  | Surge Diverter (Blue) Fault | MSB MISC ECX420-1
| MSB MISC ECX420-2 | DI | DO | AI | AO | HLI | Prog | Condition | Timing | Priority | Graphic Name | Functionality | Frequency |  |  |  |  | ECB600 Subnet |  |  |  | ECX420 | 1
Level-3 | IO-DIM6-25 |  |  | 1 | [7 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | IO-DIM6-25 |  | UI1 |  | IO-DIM6 | 1
Level-3 | FH Diesel Water Pump Run Status | 1 | [9 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | FH Diesel Water Pump Run Status | Hydraulics
Level-3 | FH Diesel Water Pump Standby Status | 1 | [13 empty] | L3 MSB |  | FH Diesel Water Pump Standby Status | Hydraulics
Level-3 | FH Diesel Water Pump Fault | 1 | [13 empty] | L3 MSB |  | FH Diesel Water Pump Fault | Hydraulics
Level-3 | FH Electric Water Pump Run Status | 1 | [13 empty] | L3 MSB |  | FH Electric Water Pump Run Status | Hydraulics
Level-3 | FH Electric Water Pump Standby Status | 1 | [13 empty] | L3 MSB |  | FH Electric Water Pump Standby Status | Hydraulics
Level-3 | FH Electric Water Pump Fault | 1 | [13 empty] | L3 MSB |  | FH Electric Water Pump Fault | Hydraulics
Level-3 | IO-DIM6-26 |  |  | 1 | [7 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | IO-DIM6-26 |  | UI2 |  | IO-DIM6 | 1
Level-3 | FS Diesel Water Pump Run Status | 1 | [9 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | FS Diesel Water Pump Run Status | Hydraulics
Level-3 | FS Diesel Water Pump Standby Status | 1 | [13 empty] | L3 MSB |  | FS Diesel Water Pump Standby Status | Hydraulics
Level-3 | FS Diesel Water Pump Fault | 1 | [13 empty] | L3 MSB |  | FS Diesel Water Pump Fault | Hydraulics
Level-3 | FS Electric Water Pump Run Status | 1 | [13 empty] | L3 MSB |  | FS Electric Water Pump Run Status | Hydraulics
Level-3 | FS Electric Water Pump Standby Status | 1 | [13 empty] | L3 MSB |  | FS Electric Water Pump Standby Status | Hydraulics
Level-3 | FS Electric Water Pump Fault | 1 | [13 empty] | L3 MSB |  | FS Electric Water Pump Fault | Hydraulics
Level-3 | IO-DIM6-27 |  |  | 1 | [7 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | IO-DIM6-27 |  | UI3 |  | IO-DIM6 | 1
Level-3 | Fire Services Water Tank 1 High Level | 1 | [9 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | Fire Services Water Tank 1 High Level | Hydraulics
Level-3 | Fire Services Water Tank 1 Low Level | 1 | [13 empty] | L3 MSB |  | Fire Services Water Tank 1 Low Level | Hydraulics
Level-3 | Fire Services Water Tank 1 Empty | 1 | [13 empty] | L3 MSB |  | Fire Services Water Tank 1 Empty | Hydraulics
Level-3 | Fire Services Water Tank 2 High Level | 1 | [13 empty] | L3 MSB |  | Fire Services Water Tank 2 High Level | Hydraulics
Level-3 | Fire Services Water Tank 2 Low Level | 1 | [13 empty] | L3 MSB |  | Fire Services Water Tank 2 Low Level | Hydraulics
Level-3 | Fire Services Water Tank 2 Empty | 1 | [13 empty] | L3 MSB |  | Fire Services Water Tank 2 Empty | Hydraulics
| Sub Total | 72 | 0 | 12 | 0 | 0 | 0
| Hydraulics | DI | DO | AI | AO | HLI | Prog | Condition | Timing | Priority | Graphic Name | Functionality | Frequency |  | ECB600 |  |  | MSSB Panel L3 |  |  |  | ECB600 | 1
Level-3 | Water Meter 1 Pulse | 1 | [5 empty] | >or< Setpoint by 5% | 15min(1Hour Inhibit) | Critical |  | Display only | COV |  | Hydraulics -UI1 | NZ F&B Actuator | Hydraulics | Water Meter 1 Pulse | Hydraulics | UI1 | Level-3 | Terminals | 1
Level-3 | Water Meter 2 Pulse | 1 | [5 empty] | >or< Setpoint by 5% | 15min(1Hour Inhibit) | Critical |  | Display only | COV |  | Hydraulics -UI2 | NZ F&B Actuator | Hydraulics | Water Meter 2 Pulse | Hydraulics | UI2 | Level-3 | Terminals | 1
Level-3 | Water Meter 3 Pulse | 1 | [5 empty] | >or< Setpoint by 5% | 15min(1Hour Inhibit) | Critical |  | Display only | COV |  | Hydraulics -UI3 | NZ F&B Actuator | Hydraulics | Water Meter 3 Pulse | Hydraulics | UI3 | Level-3 | Terminals | 1
Level-3 | UV Steriliser 2 Hours Run Counter | 1 | [5 empty] | >or< Setpoint by 5% | 15min(1Hour Inhibit) | Critical |  | Display only | COV |  | Hydraulics -UI4 | NZ F&B Actuator | Hydraulics | UV Steriliser 2 Hours Run Counter | Hydraulics | UI4 | Level-3 | Terminals | 1
Level-3 | IO-DIM6-28 |  |  | 1 | [7 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | IO-DIM6-28 |  | UI5 |  | IO-DIM6 | 1
Level-3 | Triplex Cold Water Pump 1 Run Status | 1 | [9 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | Triplex Cold Water Pump 1 Run Status | Hydraulics
Level-3 | Triplex Cold Water Pump 1 Standby Status | 1 | [13 empty] | L3 MSB |  | Triplex Cold Water Pump 1 Standby Status | Hydraulics
Level-3 | Triplex Cold Water Pump 1 Fault | 1 | [13 empty] | L3 MSB |  | Triplex Cold Water Pump 1 Fault | Hydraulics
Level-3 | Triplex Cold Water Pump 2 Run Status | 1 | [13 empty] | L3 MSB |  | Triplex Cold Water Pump 2 Run Status | Hydraulics
Level-3 | Triplex Cold Water Pump 2 Standby Status | 1 | [13 empty] | L3 MSB |  | Triplex Cold Water Pump 2 Standby Status | Hydraulics
Level-3 | Triplex Cold Water Pump 2 Fault | 1 | [13 empty] | L3 MSB |  | Triplex Cold Water Pump 2 Fault | Hydraulics
Level-3 | IO-DIM6-29 |  |  | 1 | [7 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | IO-DIM6-29 |  | UI6 |  | IO-DIM6 | 1
Level-3 | Triplex Cold Water Pump 3 Run Status | 1 | [9 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | Triplex Cold Water Pump 3 Run Status | Hydraulics
Level-3 | Triplex Cold Water Pump 3 Standby Status | 1 | [13 empty] | L3 MSB |  | Triplex Cold Water Pump 3 Standby Status | Hydraulics
Level-3 | Triplex Cold Water Pump 3 Fault | 1 | [13 empty] | L3 MSB |  | Triplex Cold Water Pump 3 Fault | Hydraulics
Level-3 | HW Circ Pump 1 Run Status | 1 | [13 empty] | L3 MSB |  | HW Circ Pump 1 Run Status | Hydraulics
Level-3 | HW Circ Pump 1 Pump Standby Status | 1 | [13 empty] | L3 MSB |  | HW Circ Pump 1 Pump Standby Status | Hydraulics
Level-3 | HW Circ Pump 1 Pump Fault | 1 | [13 empty] | L3 MSB |  | HW Circ Pump 1 Pump Fault | Hydraulics
Level-3 | IO-DIM6-30 |  |  | 1 | [7 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | IO-DIM6-30 |  | UI7 |  | IO-DIM6 | 1
Level-3 | HW Circ Pump 2 Run Status | 1 | [9 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | HW Circ Pump 2 Run Status | Hydraulics
Level-3 | HW Circ Pump 2 Pump Standby Status | 1 | [13 empty] | L3 MSB |  | HW Circ Pump 2 Pump Standby Status | Hydraulics
Level-3 | HW Circ Pump 2 Pump Fault | 1 | [13 empty] | L3 MSB |  | HW Circ Pump 2 Pump Fault | Hydraulics
Level-3 | LL Potable Water Tank 1 High Level | 1 | [13 empty] | L3 MSB |  | LL Potable Water Tank 1 High Level | Hydraulics
Level-3 | LL Potable Water Tank 1 Low Level | 1 | [13 empty] | L3 MSB |  | LL Potable Water Tank 1 Low Level | Hydraulics
Level-3 | LL Potable Water Tank 1 Empty | 1 | [13 empty] | L3 MSB |  | LL Potable Water Tank 1 Empty | Hydraulics
Level-3 | IO-DIM6-31 |  |  | 1 | [7 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | IO-DIM6-31 |  | UI8 |  | IO-DIM6 | 1
Level-3 | LL Potable Water Tank 2 High Level | 1 | [9 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | LL Potable Water Tank 2 High Level | Hydraulics
Level-3 | LL Potable Water Tank 2 Low Level | 1 | [13 empty] | L3 MSB |  | LL Potable Water Tank 2 Low Level | Hydraulics
Level-3 | LL Potable Water Tank 2 Empty | 1 | [13 empty] | L3 MSB |  | LL Potable Water Tank 2 Empty | Hydraulics
Level-3 | Water Treatment St1 Filter 1 Run Status | 1 | [13 empty] | L3 MSB |  | Water Treatment St1 Filter 1 Run Status | Hydraulics
Level-3 | Water Treatment St1 Filter 1 Backwash Status | 1 | [13 empty] | L3 MSB |  | Water Treatment St1 Filter 1 Backwash Status | Hydraulics
Level-3 | Water Treatment St1 Filter 2 Run Status | 1 | [13 empty] | L3 MSB |  | Water Treatment St1 Filter 2 Run Status | Hydraulics
Level-3 | IO-DIM6-32 |  |  | 1 | [7 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | IO-DIM6-32 |  | UI9 |  | IO-DIM6 | 1
Level-3 | Water Treatment St1 Filter 2 Backwash Status | 1 | [9 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | Water Treatment St1 Filter 2 Backwash Status | Hydraulics
Level-3 | Water Treatment St3 Filter 1 Run Status | 1 | [13 empty] | L3 MSB |  | Water Treatment St3 Filter 1 Run Status | Hydraulics
Level-3 | Water Treatment St3 Filter 1 Fault | 1 | [13 empty] | L3 MSB |  | Water Treatment St3 Filter 1 Fault | Hydraulics
Level-3 | Water Treatment St3 Filter 2 Run Status | 1 | [13 empty] | L3 MSB |  | Water Treatment St3 Filter 2 Run Status | Hydraulics
Level-3 | Water Treatment St3 Filter 2 Fault | 1 | [13 empty] | L3 MSB |  | Water Treatment St3 Filter 2 Fault | Hydraulics
Level-3 | Spare | [14 empty] | L3 MSB |  | Spare | Hydraulics
Level-3 | IO-DIM6-33 |  |  | 1 | [7 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | IO-DIM6-33 |  | UI10 |  | IO-DIM6 | 1
Level-3 | Haemodialysis Water Treatment Sys1 Run Ststus | 1 | [9 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | Haemodialysis Water Treatment Sys1 Run Ststus | Hydraulics
Level-3 | Haemodialysis Water Treatment Sys1 Fault | 1 | [13 empty] | L3 MSB |  | Haemodialysis Water Treatment Sys1 Fault | Hydraulics
Level-3 | Haemodialysis Water Treatment Sys2 Run Ststus | 1 | [13 empty] | L3 MSB |  | Haemodialysis Water Treatment Sys2 Run Ststus | Hydraulics
Level-3 | Haemodialysis Water Treatment Sys2 Fault | 1 | [13 empty] | L3 MSB |  | Haemodialysis Water Treatment Sys2 Fault | Hydraulics
Level-3 | Haemodialysis Water Treatment Sys3 Run Ststus | 1 | [13 empty] | L3 MSB |  | Haemodialysis Water Treatment Sys3 Run Ststus | Hydraulics
Level-3 | Haemodialysis Water Treatment Sys3 Fault | 1 | [13 empty] | L3 MSB |  | Haemodialysis Water Treatment Sys3 Fault | Hydraulics
Level-3 | IO-DIM6-34 |  |  | 1 | [7 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | IO-DIM6-34 |  | UI11 |  | IO-DIM6 | 1
Level-3 | TMV Monitor Hub Server Warning | 1 | [9 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | TMV Monitor Hub Server Warning | Hydraulics
Level-3 | TMV Monitor Hub Server Fault | 1 | [13 empty] | L3 MSB |  | TMV Monitor Hub Server Fault | Hydraulics
Level-3 | Gas Interlock Open | 1 | [13 empty] | L3 MSB |  | Gas Interlock Open | Hydraulics
Level-3 | Gas Interlock Close | 1 | [13 empty] | L3 MSB |  | Gas Interlock Close | Hydraulics
Level-3 | [15 empty] | L3 MSB |  | 0 | Hydraulics
Level-3 | [15 empty] | L3 MSB |  | 0 | Hydraulics
Level-3 | IO-DIM6-35 |  |  | 1 | [7 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | IO-DIM6-35 |  | UI12 |  | IO-DIM6 | 1
Level-3 | DIFFS Diesel Water Pump Run Status | 1 | [9 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | DIFFS Diesel Water Pump Run Status | Hydraulics
Level-3 | DIFFS Diesel Water Pump Standby Status | 1 | [13 empty] | L3 MSB |  | DIFFS Diesel Water Pump Standby Status | Hydraulics
Level-3 | DIFFS Diesel Water Pump Fault | 1 | [13 empty] | L3 MSB |  | DIFFS Diesel Water Pump Fault | Hydraulics
Level-3 | DIFFS Electric Water Pump Run Status | 1 | [13 empty] | L3 MSB |  | DIFFS Electric Water Pump Run Status | Hydraulics
Level-3 | DIFFS Electric Water Pump Standby Status | 1 | [13 empty] | L3 MSB |  | DIFFS Electric Water Pump Standby Status | Hydraulics
Level-3 | DIFFS Electric Water Pump Fault | 1 | [13 empty] | L3 MSB |  | DIFFS Electric Water Pump Fault | Hydraulics
Level-3 | IO-DIM6-36 |  |  | 1 | [7 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | IO-DIM6-36 |  | UI13 |  | IO-DIM6 | 1
Level-3 | DIFFS Water Tank 1 High Level | 1 | [9 empty] | Display & Override | 10 Min or > 5% COV |  |  | L3 MSB |  | DIFFS Water Tank 1 High Level | Hydraulics
Level-3 | DIFFS Water Tank 1 Low Level | 1 | [13 empty] | L3 MSB |  | DIFFS Water Tank 1 Low Level | Hydraulics
Level-3 | DIFFS Water Tank 1 Empty | 1 | [13 empty] | L3 MSB |  | DIFFS Water Tank 1 Empty | Hydraulics
Level-3 | DIFFS Water Tank 2 High Level | 1 | [13 empty] | L3 MSB |  | DIFFS Water Tank 2 High Level | Hydraulics
Level-3 | DIFFS Water Tank 2 Low Level | 1 | [13 empty] | L3 MSB |  | DIFFS Water Tank 2 Low Level | Hydraulics
Level-3 | DIFFS Water Tank 2 Empty | 1 | [13 empty] | L3 MSB |  | DIFFS Water Tank 2 Empty | Hydraulics
| Sub Total | 55 | 0 | 9 | 0 | 0 | 0
[8 empty] | Alarms |  |  | Graphics |  | History Data
Level 4
Comms Rooms 4108
Level-4 | FCU-L4-01 | DI | DO | AI | AO | HLI | Prog | Condition | Timing | Priority | Graphic Name | Functionality | Frequency | [8 empty] | ECB203 | 1
Level-4 | Schedule | [5 empty] | 1 |  |  |  | FCU | Display & Override | 10 Min or > 5% COV |  | FCU-L4-01-SW01 | Level-4 | FCU-L4-01 | Schedule | FCU-L4-01 | SW01 | Software | Software Point | 1
Level-4 | Fan Enable |  | 1 | [8 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L4-01-DO1 | Level-4 | FCU-L4-01 | Fan Enable | FCU-L4-01 | DO1 | MSSB | 24VAC Relay | 1
Level-4 | GEF-L4-04 Fan Enable |  | 1 | [8 empty] | Display & Override | 10 Min or > 5% COV |  | GEF-L4-04-DO2 | Level-3 | GEF-L4-04 | GEF-L4-04 Fan Enable | GEF-L4-04 | DO2 | MSSB | 24VAC Relay | 1
Level-4 | Fan Status | 1 | [5 empty] | Mismatch with enable | 60s | Critical |  | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L4-01-UI1 | Level-4 | FCU-L4-01 | Fan Status | FCU-L4-01 | UI1 | MSSB | CCS | 1
Level-4 | SA Temp |  |  | 1 | [7 empty] | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L4-01-UI2 | Level-4 | FCU-L4-01 | SA Temp | FCU-L4-01 | UI2 | SA Ductwork | PDIGR-TE200BE24B2 | 1
Level-4 | Space Temp |  |  | 1 |  |  |  | >or< Setpoint by 2°C | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 11 Min or > 5% COV |  | FCU-L4-01-UI3 | Level-4 | FCU-L4-01 | Space Temp | FCU-L4-01 | UI3 | Space | PDITE-SENSORX0 | 1
Level-4 | Dirty Filter | 1 | [5 empty] | Change of State | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L4-01-UI4 | Level-4 | FCU-L4-01 | Dirty Filter | FCU-L4-01 | UI4 | Filter Box | AFS - 930.80222524 | 1
Level-4 | GEF-L4-04 Status | 1 | [12 empty] | GEF-L4-04-UI5 | Level-4 | GEF-L4-04 | GEF-L4-04 Status | GEF-L4-04 | UI5 | MSSB | CCS | 1
Level-4 | Fire | 1 | [5 empty] | COS | 0s | Fire |  | Display / Red on Alarm | 10 Min or > 5% COV |  | L4 Fire signal-UI5 | Level-4 | L4 Fire signal | Fire | L4 Fire signal | UI5 | MSSB | 24VAC Relay | 1
Level-4 | CHW Valve |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L4-01-UO6 | Level-4 | FCU-L4-01 | CHW Valve | FCU-L4-01 | UO6 | FCU | CHWV Actuator | 1
Level-4 | Fan Speed |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L4-01-UO8 | Level-4 | FCU-L4-01 | Fan Speed | FCU-L4-01 | UO8 | FCU | Terminals | 1
| Sub Total | 4 | 2 | 2 | 2 | 0 | 1
Lift Lobby and Corridor Areas 4C07
Level-4 | FCU-L4-02 | DI | DO | AI | AO | HLI | Prog | Condition | Timing | Priority | Graphic Name | Functionality | Frequency | [8 empty] | ECB203 | 1
Level-4 | Schedule | [5 empty] | 1 |  |  |  | FCU | Display & Override | 10 Min or > 5% COV |  | FCU-L4-02-SW01 | Level-4 | FCU-L4-02 | Schedule | FCU-L4-02 | SW01 | Software | Software Point | 1
Level-4 | Fan Enable |  | 1 | [8 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L4-02-DO1 | Level-4 | FCU-L4-02 | Fan Enable | FCU-L4-02 | DO1 | MSSB | 24VAC Relay | 1
Level-4 | OAF-L4-01 Fan Enable |  | 1 | [8 empty] | Display & Override | 10 Min or > 5% COV |  | OAF-L4-01-DO2 | Level-4 | OAF-L4-01 | OAF-L4-01 Fan Enable | OAF-L4-01 | DO2 | MSSB | 24VAC Relay | 1
Level-4 | OAF-L4-02 Fan Enable |  | 1 | [8 empty] | Display & Override | 10 Min or > 5% COV |  | OAF-L4-02-DO3 | Level-4 | OAF-L4-02 | OAF-L4-02 Fan Enable | OAF-L4-02 | DO3 | MSSB | 24VAC Relay | 1
Level-4 | Fan Status | 1 | [5 empty] | Mismatch with enable | 60s | Critical |  | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L4-02-UI1 | Level-4 | FCU-L4-02 | Fan Status | FCU-L4-02 | UI1 | MSSB | CCS | 1
Level-4 | SA Temp |  |  | 1 | [7 empty] | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L4-02-UI2 | Level-4 | FCU-L4-02 | SA Temp | FCU-L4-02 | UI2 | SA Ductwork | PDIGR-TE200BE24B2 | 1
Level-4 | RA Temp |  |  | 1 |  |  |  | >or< Setpoint by 2°C | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 11 Min or > 5% COV |  | FCU-L4-02-UI3 | Level-4 | FCU-L4-02 | RA Temp | FCU-L4-02 | UI3 | RA Ductwork | PDIGR-TE200BE24B2 | 1
Level-4 | Dirty Filter | 1 | [5 empty] | Change of State | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L4-02-UI4 | Level-4 | FCU-L4-02 | Dirty Filter | FCU-L4-02 | UI4 | Filter Box | AFS - 930.80222524 | 1
Level-4 | OAF-L4-01 Status | 1 | [12 empty] | OAF-L4-01-UI5 | Level-4 | OAF-L4-01 | OAF-L4-01 Status | OAF-L4-01 | UI5 | MSSB | CCS | 1
Level-4 | OAF-L4-02 Status | 1 | [12 empty] | OAF-L4-02-UI6 | Level-4 | OAF-L4-02 | OAF-L4-02 Status | OAF-L4-02 | UI6 | MSSB | CCS | 1
Level-4 | CHW Valve |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L4-02-UO6 | Level-4 | FCU-L4-02 | CHW Valve | FCU-L4-02 | UO6 | FCU | CHWV Actuator | 1
Level-4 | HW Valve |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L4-02-UO7 | Level-4 | FCU-L4-02 | HW Valve | FCU-L4-02 | UO7 | FCU | HHWV Actuator | 1
| Sub Total | 4 | 3 | 2 | 2 | 0 | 1
Lift Lobby and Corridor Areas
Level-4 | FCU-L4-03 | DI | DO | AI | AO | HLI | Prog | Condition | Timing | Priority | Graphic Name | Functionality | Frequency | [8 empty] | ECB203 | 1
Level-4 | Schedule | [5 empty] | 1 |  |  |  | FCU | Display & Override | 10 Min or > 5% COV |  | FCU-L4-03-SW01 | Level-4 | FCU-L4-03 | Schedule | FCU-L4-03 | SW01 | Software | Software Point | 1
Level-4 | Fan Enable |  | 1 | [8 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L4-03-DO1 | Level-4 | FCU-L4-03 | Fan Enable | FCU-L4-03 | DO1 | MSSB | 24VAC Relay | 1
Level-4 | Fan Status | 1 | [5 empty] | Mismatch with enable | 60s | Critical |  | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L4-03-UI1 | Level-4 | FCU-L4-03 | Fan Status | FCU-L4-03 | UI1 | MSSB | CCS | 1
Level-4 | SA Temp |  |  | 1 | [7 empty] | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L4-03-UI2 | Level-4 | FCU-L4-03 | SA Temp | FCU-L4-03 | UI2 | SA Ductwork | PDIGR-TE200BE24B2 | 1
Level-4 | RA Temp |  |  | 1 |  |  |  | >or< Setpoint by 2°C | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 11 Min or > 5% COV |  | FCU-L4-03-UI3 | Level-4 | FCU-L4-03 | RA Temp | FCU-L4-03 | UI3 | RA Ductwork | PDIGR-TE200BE24B2 | 1
Level-4 | Dirty Filter | 1 | [5 empty] | Change of State | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L4-03-UI4 | Level-4 | FCU-L4-03 | Dirty Filter | FCU-L4-03 | UI4 | Filter Box | AFS - 930.80222524 | 1
Level-4 | CHW Valve |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L4-03-UO6 | Level-4 | FCU-L4-03 | CHW Valve | FCU-L4-03 | UO6 | FCU | CHWV Actuator | 1
Level-4 | HW Valve |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L4-03-UO7 | Level-4 | FCU-L4-03 | HW Valve | FCU-L4-03 | UO7 | FCU | HHWV Actuator | 1
[12 empty] | Display & Override | 10 Min or > 5% COV | [6 empty] | UO8
-
| Sub Total | 2 | 1 | 2 | 2 | 0 | 1
Renal Department - Fluids 4093
Level-4 | FCU-L4-04 | DI | DO | AI | AO | HLI | Prog | Condition | Timing | Priority | Graphic Name | Functionality | Frequency | [8 empty] | ECB203 | 1
Level-4 | Schedule | [5 empty] | 1 |  |  |  | FCU | Display & Override | 10 Min or > 5% COV |  | FCU-L4-04-SW01 | Level-4 | FCU-L4-04 | Schedule | FCU-L4-04 | SW01 | Software | Software Point | 1
Level-4 | Fan Enable |  | 1 | [8 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L4-04-DO1 | Level-4 | FCU-L4-04 | Fan Enable | FCU-L4-04 | DO1 | MSSB | 24VAC Relay | 1
Level-4 | Fan Status | 1 | [5 empty] | Mismatch with enable | 60s | Critical |  | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L4-04-UI1 | Level-4 | FCU-L4-04 | Fan Status | FCU-L4-04 | UI1 | MSSB | CCS | 1
Level-4 | SA Temp |  |  | 1 | [7 empty] | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L4-04-UI2 | Level-4 | FCU-L4-04 | SA Temp | FCU-L4-04 | UI2 | SA Ductwork | PDIGR-TE200BE24B2 | 1
Level-4 | RA Temp |  |  | 1 |  |  |  | >or< Setpoint by 2°C | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 11 Min or > 5% COV |  | FCU-L4-04-UI3 | Level-4 | FCU-L4-04 | RA Temp | FCU-L4-04 | UI3 | RA Ductwork | PDIGR-TE200BE24B2 | 1
Level-4 | Dirty Filter | 1 | [5 empty] | Change of State | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L4-04-UI4 | Level-4 | FCU-L4-04 | Dirty Filter | FCU-L4-04 | UI4 | Filter Box | AFS - 930.80222524 | 1
Level-4 | Fire | 1 | [5 empty] | COS | 0s | Fire |  | Display / Red on Alarm | 10 Min or > 5% COV |  | L4 Fire signal-UI5 | Level-4 | L4 Fire signal | Fire | L4 Fire signal | UI5 | MSSB | 24VAC Relay | 1
Level-4 | CHW Valve |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L4-04-UO6 | Level-4 | FCU-L4-04 | CHW Valve | FCU-L4-04 | UO6 | FCU | CHWV Actuator | 1
Level-4 | HW Valve |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L4-04-UO7 | Level-4 | FCU-L4-04 | HW Valve | FCU-L4-04 | UO7 | FCU | HHWV Actuator | 1
| Sub Total | 3 | 1 | 2 | 2 | 0 | 1
Renal - Main Waiting Area
Level-4 | FCU-L4-RN-01 | DI | DO | AI | AO | HLI | Prog | Condition | Timing | Priority | Graphic Name | Functionality | Frequency | [8 empty] | ECB300 | 1
Level-4 | Schedule | [5 empty] | 1 |  |  |  | FCU | Display & Override | 10 Min or > 5% COV |  | FCU-L4-RN-01-SW01 | Level-4 | FCU-L4-RN-01 | Schedule | FCU-L4-RN-01 | SW01 | Software | Software Point | 1
Level-4 | Fan Enable |  | 1 | [8 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L4-RN-01-UO1 | Level-4 | FCU-L4-RN-01 | Fan Enable | FCU-L4-RN-01 | UO1 | MSSB | 12VDC Relay | 1
Level-4 | Fan Status | 1 | [5 empty] | Mismatch with enable | 60s | Critical |  | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L4-RN-01-UI1 | Level-4 | FCU-L4-RN-01 | Fan Status | FCU-L4-RN-01 | UI1 | MSSB | CCS | 1
Level-4 | SA Temp |  |  | 1 | [7 empty] | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L4-RN-01-UI2 | Level-4 | FCU-L4-RN-01 | SA Temp | FCU-L4-RN-01 | UI2 | SA Ductwork | PDIGR-TE200BE24B2 | 1
Level-4 | Space Temp |  |  | 1 |  |  |  | >or< Setpoint by 2°C | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 11 Min or > 5% COV |  | FCU-L4-RN-01-UI3 | Level-4 | FCU-L4-RN-01 | Space Temp | FCU-L4-RN-01 | UI3 | Space | PDITE-SENSORX0 | 1
Level-4 | Dirty Filter | 1 | [5 empty] | Change of State | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L4-RN-01-UI4 | Level-4 | FCU-L4-RN-01 | Dirty Filter | FCU-L4-RN-01 | UI4 | Filter Box | AFS - 930.80222524 | 1
Level-4 | WZ Space Temp |  |  | 1 |  |  |  | >or< Setpoint by 2°C | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | AHU-L4-RN-WZ-UI5 | Level-4 | AHU-L4-RN-WZ | WZ Space Temp | AHU-L4-RN-WZ | UI5 | Space | PDITE-SENSORX0 | 1
Level-4 | CZ Space Temp 1 |  |  | 1 |  |  |  | >or< Setpoint by 2°C | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | AHU-L4-RN-CZ-UI6 | Level-4 | AHU-L4-RN-CZ | CZ Space Temp 1 | AHU-L4-RN-CZ | UI6 | Space | PDITE-SENSORX0 | 1
Level-4 | AH LED WZ-RN |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | AHU-L4-RN-WZ-UO4 | Level-4 | AHU-L4-RN-WZ | AH LED WZ-RN | AHU-L4-RN-WZ | UO4 | FCU | PDITE-SENSORX0 | 0
Level-4 | AH LED CZ1-RN |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | AHU-L4-RN-CZ-UO5 | Level-4 | AHU-L4-RN-CZ | AH LED CZ1-RN | AHU-L4-RN-CZ | UO5 | FCU | PDITE-SENSORX0 | 0
Level-4 | CHW Valve |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L4-RN-01-UO6 | Level-4 | FCU-L4-RN-01 | CHW Valve | FCU-L4-RN-01 | UO6 | FCU | CHWV Actuator | 1
Level-4 | HW Valve |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L4-RN-01-UO7 | Level-4 | FCU-L4-RN-01 | HW Valve | FCU-L4-RN-01 | UO7 | FCU | HHWV Actuator | 1
| Sub Total | 2 | 1 | 4 | 4 | 0 | 1
Renal - Meeting Room
Level-4 | FCU-L4-RN-02 | DI | DO | AI | AO | HLI | Prog | Condition | Timing | Priority | Graphic Name | Functionality | Frequency | [8 empty] | ECB203 | 1
Level-4 | Schedule | [5 empty] | 1 |  |  |  | FCU | Display & Override | 10 Min or > 5% COV |  | FCU-L4-RN-02-SW01 | Level-4 | FCU-L4-RN-02 | Schedule | FCU-L4-RN-02 | SW01 | Software | Software Point | 1
Level-4 | Fan Enable |  | 1 | [8 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L4-RN-02-DO1 | Level-4 | FCU-L4-RN-02 | Fan Enable | FCU-L4-RN-02 | DO1 | MSSB | 24VAC Relay | 1
Level-4 | Fan Status | 1 | [5 empty] | Mismatch with enable | 60s | Critical |  | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L4-RN-02-UI1 | Level-4 | FCU-L4-RN-02 | Fan Status | FCU-L4-RN-02 | UI1 | MSSB | CCS | 1
Level-4 | SA Temp |  |  | 1 | [7 empty] | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L4-RN-02-UI2 | Level-4 | FCU-L4-RN-02 | SA Temp | FCU-L4-RN-02 | UI2 | SA Ductwork | PDIGR-TE200BE24B2 | 1
Level-4 | RA Temp |  |  | 1 |  |  |  | >or< Setpoint by 2°C | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 11 Min or > 5% COV |  | FCU-L4-RN-02-UI3 | Level-4 | FCU-L4-RN-02 | RA Temp | FCU-L4-RN-02 | UI3 | RA Ductwork | PDIGR-TE200BE24B2 | 1
Level-4 | Dirty Filter | 1 | [5 empty] | Change of State | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L4-RN-02-UI4 | Level-4 | FCU-L4-RN-02 | Dirty Filter | FCU-L4-RN-02 | UI4 | Filter Box | AFS - 930.80222524 | 1
Level-4 | Small Drug Fridge Temp (Rm 4081 Clean Utility) |  |  | 1 | [7 empty] | Display / Red on Alarm | 10 Min or > 5% COV |  | Fridges-UI5 | Level 5 | Fridges | Small Drug Fridge Temp (Rm 4081 Clean Utility) | Fridges | UI5 | Space | PDIGR-TE200BE24B2 | 1
Level-4 | Small Drug Fridge Fault (Rm 4081 Clean Utility) | 1 | [5 empty] | Change of State | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | Fridges-UI6 | Level 5 | Fridges | Small Drug Fridge Fault (Rm 4081 Clean Utility) | Fridges | UI6 | Space | Terminals | 1
Level-4 | CHW Valve |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L4-RN-02-UO6 | Level-4 | FCU-L4-RN-02 | CHW Valve | FCU-L4-RN-02 | UO6 | FCU | CHWV Actuator | 1
Level-4 | HW Valve |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L4-RN-02-UO7 | Level-4 | FCU-L4-RN-02 | HW Valve | FCU-L4-RN-02 | UO7 | FCU | HHWV Actuator | 1
| Sub Total | 3 | 1 | 3 | 2 | 0 | 1
Renal - Group Training Room
Level-4 | FCU-L4-RN-03 | DI | DO | AI | AO | HLI | Prog | Condition | Timing | Priority | Graphic Name | Functionality | Frequency | [8 empty] | ECB300 | 1
Level-4 | Schedule | [5 empty] | 1 |  |  |  | FCU | Display & Override | 10 Min or > 5% COV |  | FCU-L4-RN-03-SW01 | Level-4 | FCU-L4-RN-03 | Schedule | FCU-L4-RN-03 | SW01 | Software | Software Point | 1
Level-4 | Fan Enable |  | 1 | [8 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L4-RN-03-UO1 | Level-4 | FCU-L4-RN-03 | Fan Enable | FCU-L4-RN-03 | UO1 | MSSB | 12VDC Relay | 1
Level-4 | Fan Status | 1 | [5 empty] | Mismatch with enable | 60s | Critical |  | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L4-RN-03-UI1 | Level-4 | FCU-L4-RN-03 | Fan Status | FCU-L4-RN-03 | UI1 | MSSB | CCS | 1
Level-4 | SA Temp |  |  | 1 | [7 empty] | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L4-RN-03-UI2 | Level-4 | FCU-L4-RN-03 | SA Temp | FCU-L4-RN-03 | UI2 | SA Ductwork | PDIGR-TE200BE24B2 | 1
Level-4 | RA Temp |  |  | 1 |  |  |  | >or< Setpoint by 2°C | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 11 Min or > 5% COV |  | FCU-L4-RN-03-UI3 | Level-4 | FCU-L4-RN-03 | RA Temp | FCU-L4-RN-03 | UI3 | RA Ductwork | PDIGR-TE200BE24B2 | 1
Level-4 | Dirty Filter | 1 | [5 empty] | Change of State | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L4-RN-03-UI4 | Level-4 | FCU-L4-RN-03 | Dirty Filter | FCU-L4-RN-03 | UI4 | Filter Box | AFS - 930.80222524 | 1
Level-4 | SZ Space Temp |  |  | 1 |  |  |  | >or< Setpoint by 2°C | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 11 Min or > 5% COV |  | AHU-L4-RN-SZ-UI5 | Level-4 | AHU-L4-RN-SZ | SZ Space Temp | AHU-L4-RN-SZ | UI5 | Space | PDITE-SENSORX0 | 1
Level-4 | CZ Space Temp 2 |  |  | 1 |  |  |  | >or< Setpoint by 2°C | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | AHU-L4-RN-CZ-UI6 | Level-4 | AHU-L4-RN-CZ | CZ Space Temp 2 | AHU-L4-RN-CZ | UI6 | Space | PDITE-SENSORX0 | 1
Level-4 | AH LED SZ-RN |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | AHU-L4-RN-SZ-UO4 | Level-4 | AHU-L4-RN-SZ | AH LED SZ-RN | AHU-L4-RN-SZ | UO4 | FCU | PDITE-SENSORX0 | 0
Level-4 | AH LED CZ2-RN |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | AHU-L4-RN-CZ-UO5 | Level-4 | AHU-L4-RN-CZ | AH LED CZ2-RN | AHU-L4-RN-CZ | UO5 | FCU | PDITE-SENSORX0 | 0
Level-4 | CHW Valve |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L4-RN-03-UO6 | Level-4 | FCU-L4-RN-03 | CHW Valve | FCU-L4-RN-03 | UO6 | FCU | CHWV Actuator | 1
Level-4 | HW Valve |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L4-RN-03-UO7 | Level-4 | FCU-L4-RN-03 | HW Valve | FCU-L4-RN-03 | UO7 | FCU | HHWV Actuator | 1
| Sub Total | 2 | 1 | 4 | 4 | 0 | 1
Renal - Staff Resource Room
Level-4 | FCU-L4-RN-04 | DI | DO | AI | AO | HLI | Prog | Condition | Timing | Priority | Graphic Name | Functionality | Frequency | [8 empty] | ECB203 | 1
Level-4 | Schedule | [5 empty] | 1 |  |  |  | FCU | Display & Override | 10 Min or > 5% COV |  | FCU-L4-RN-04-SW01 | Level-4 | FCU-L4-RN-04 | Schedule | FCU-L4-RN-04 | SW01 | Software | Software Point | 1
Level-4 | Fan Enable |  | 1 | [8 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L4-RN-04-DO1 | Level-4 | FCU-L4-RN-04 | Fan Enable | FCU-L4-RN-04 | DO1 | MSSB | 24VAC Relay | 1
Level-4 | Fan Status | 1 | [5 empty] | Mismatch with enable | 60s | Critical |  | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L4-RN-04-UI1 | Level-4 | FCU-L4-RN-04 | Fan Status | FCU-L4-RN-04 | UI1 | MSSB | CCS | 1
Level-4 | SA Temp |  |  | 1 | [7 empty] | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L4-RN-04-UI2 | Level-4 | FCU-L4-RN-04 | SA Temp | FCU-L4-RN-04 | UI2 | SA Ductwork | PDIGR-TE200BE24B2 | 1
Level-4 | RA Temp |  |  | 1 |  |  |  | >or< Setpoint by 2°C | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 11 Min or > 5% COV |  | FCU-L4-RN-04-UI3 | Level-4 | FCU-L4-RN-04 | RA Temp | FCU-L4-RN-04 | UI3 | RA Ductwork | PDIGR-TE200BE24B2 | 1
Level-4 | Dirty Filter | 1 | [5 empty] | Change of State | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L4-RN-04-UI4 | Level-4 | FCU-L4-RN-04 | Dirty Filter | FCU-L4-RN-04 | UI4 | Filter Box | AFS - 930.80222524 | 1
Level-4 | Large Drug Fridge Temp (Rm 4081 Clean Utility) |  |  | 1 | [7 empty] | Display / Red on Alarm | 10 Min or > 5% COV |  | Fridges-UI5 | Level 5 | Fridges | Large Drug Fridge Temp (Rm 4081 Clean Utility) | Fridges | UI5 | Space | PDIGR-TE200BE24B2 | 1
Level-4 | Large Drug Fridge Fault (Rm 4081 Clean Utility) | 1 | [5 empty] | Change of State | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | Fridges-UI6 | Level 5 | Fridges | Large Drug Fridge Fault (Rm 4081 Clean Utility) | Fridges | UI6 | Space | Terminals | 1
Level-4 | CHW Valve |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L4-RN-04-UO6 | Level-4 | FCU-L4-RN-04 | CHW Valve | FCU-L4-RN-04 | UO6 | FCU | CHWV Actuator | 1
Level-4 | HW Valve |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L4-RN-04-UO7 | Level-4 | FCU-L4-RN-04 | HW Valve | FCU-L4-RN-04 | UO7 | FCU | HHWV Actuator | 1
| Sub Total | 3 | 1 | 3 | 2 | 0 | 1
Emergency Department Support - Staff Room
Level-4 | FCU-L4-EDS-01 | DI | DO | AI | AO | HLI | Prog | Condition | Timing | Priority | Graphic Name | Functionality | Frequency | [8 empty] | ECB300 | 1
Level-4 | Schedule | [5 empty] | 1 |  |  |  | FCU | Display & Override | 10 Min or > 5% COV |  | FCU-L4-EDS-01-SW01 | Level-4 | FCU-L4-EDS-01 | Schedule | FCU-L4-EDS-01 | SW01 | Software | Software Point | 1
Level-4 | Fan Enable |  | 1 | [8 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L4-EDS-01-UO1 | Level-4 | FCU-L4-EDS-01 | Fan Enable | FCU-L4-EDS-01 | UO1 | MSSB | 12VDC Relay | 1
Level-4 | Fan Status | 1 | [5 empty] | Mismatch with enable | 60s | Critical |  | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L4-EDS-01-UI1 | Level-4 | FCU-L4-EDS-01 | Fan Status | FCU-L4-EDS-01 | UI1 | MSSB | CCS | 1
Level-4 | SA Temp |  |  | 1 | [7 empty] | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L4-EDS-01-UI2 | Level-4 | FCU-L4-EDS-01 | SA Temp | FCU-L4-EDS-01 | UI2 | SA Ductwork | PDIGR-TE200BE24B2 | 1
Level-4 | RA Temp |  |  | 1 |  |  |  | >or< Setpoint by 2°C | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 11 Min or > 5% COV |  | FCU-L4-EDS-01-UI3 | Level-4 | FCU-L4-EDS-01 | RA Temp | FCU-L4-EDS-01 | UI3 | RA Ductwork | PDIGR-TE200BE24B2 + well | 1
Level-4 | Dirty Filter | 1 | [5 empty] | Change of State | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L4-EDS-01-UI4 | Level-4 | FCU-L4-EDS-01 | Dirty Filter | FCU-L4-EDS-01 | UI4 | Filter Box | AFS - 930.80222524 | 1
Level-4 | NZ Space Temp |  |  | 1 |  |  |  | >or< Setpoint by 2°C | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | AHU-L4-EDS-NZ-UI5 | Level-4 | AHU-L4-EDS-NZ | NZ Space Temp | AHU-L4-EDS-NZ | UI5 | Space | PDITE-SENSORX0 | 1
Level-4 | CZ Space Temp |  |  | 1 |  |  |  | >or< Setpoint by 2°C | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | AHU-L4-EDS-CZ-UI6 | Level-4 | AHU-L4-EDS-CZ | CZ Space Temp | AHU-L4-EDS-CZ | UI6 | Space | PDITE-SENSORX0 | 1
Level-4 | AH LED NZ-EDS |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | AHU-L4-EDS-NZ-UO4 | Level-4 | AHU-L4-EDS-NZ | AH LED NZ-EDS | AHU-L4-EDS-NZ | UO4 | FCU | PDITE-SENSORX0 | 0
Level-4 | AH LED CZ-EDS |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | AHU-L4-EDS-CZ-UO5 | Level-4 | AHU-L4-EDS-CZ | AH LED CZ-EDS | AHU-L4-EDS-CZ | UO5 | FCU | PDITE-SENSORX0 | 0
Level-4 | CHW Valve |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L4-EDS-01-UO6 | Level-4 | FCU-L4-EDS-01 | CHW Valve | FCU-L4-EDS-01 | UO6 | FCU | CHWV Actuator | 1
Level-4 | HW Valve |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L4-EDS-01-UO7 | Level-4 | FCU-L4-EDS-01 | HW Valve | FCU-L4-EDS-01 | UO7 | FCU | HHWV Actuator | 1
| Sub Total | 2 | 1 | 4 | 4 | 0 | 1
Emergency Department Support - Meeting Room
Level-4 | FCU-L4-EDS-02 | DI | DO | AI | AO | HLI | Prog | Condition | Timing | Priority | Graphic Name | Functionality | Frequency | [8 empty] | ECB203 | 1
Level-4 | Schedule | [5 empty] | 1 |  |  |  | FCU | Display & Override | 10 Min or > 5% COV |  | FCU-L4-EDS-02-SW01 | Level-4 | FCU-L4-EDS-02 | Schedule | FCU-L4-EDS-02 | SW01 | Software | Software Point | 1
Level-4 | Fan Enable |  | 1 | [8 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L4-EDS-02-DO1 | Level-4 | FCU-L4-EDS-02 | Fan Enable | FCU-L4-EDS-02 | DO1 | MSSB | 24VAC Relay | 1
Level-4 | Fan Status | 1 | [5 empty] | Mismatch with enable | 60s | Critical |  | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L4-EDS-02-UI1 | Level-4 | FCU-L4-EDS-02 | Fan Status | FCU-L4-EDS-02 | UI1 | MSSB | CCS | 1
Level-4 | SA Temp |  |  | 1 | [7 empty] | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L4-EDS-02-UI2 | Level-4 | FCU-L4-EDS-02 | SA Temp | FCU-L4-EDS-02 | UI2 | SA Ductwork | PDIGR-TE200BE24B2 | 1
Level-4 | RA Temp |  |  | 1 |  |  |  | >or< Setpoint by 2°C | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 11 Min or > 5% COV |  | FCU-L4-EDS-02-UI3 | Level-4 | FCU-L4-EDS-02 | RA Temp | FCU-L4-EDS-02 | UI3 | RA Ductwork | PDIGR-TE200BE24B2 | 1
Level-4 | Dirty Filter | 1 | [5 empty] | Change of State | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L4-EDS-02-UI4 | Level-4 | FCU-L4-EDS-02 | Dirty Filter | FCU-L4-EDS-02 | UI4 | Filter Box | AFS - 930.80222524 | 1
Level-4 | CHW Valve |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L4-EDS-02-UO6 | Level-4 | FCU-L4-EDS-02 | CHW Valve | FCU-L4-EDS-02 | UO6 | FCU | CHWV Actuator | 1
Level-4 | HW Valve |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L4-EDS-02-UO7 | Level-4 | FCU-L4-EDS-02 | HW Valve | FCU-L4-EDS-02 | UO7 | FCU | HHWV Actuator | 1
| Sub Total | 2 | 1 | 2 | 2 | 0 | 1
Mortuary – Office / Waiting / Viewing
Level-4 | FCU-L4-MO-01 | DI | DO | AI | AO | HLI | Prog | Condition | Timing | Priority | Graphic Name | Functionality | Frequency | [8 empty] | ECB203 | 1
Level-4 | Schedule | [5 empty] | 1 |  |  |  | FCU | Display & Override | 10 Min or > 5% COV |  | FCU-L4-MO-01-SW01 | Level-4 | FCU-L4-MO-01 | Schedule | FCU-L4-MO-01 | SW01 | Software | Software Point | 1
Level-4 | Fan Enable |  | 1 | [8 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L4-MO-01-DO1 | Level-4 | FCU-L4-MO-01 | Fan Enable | FCU-L4-MO-01 | DO1 | MSSB | 24VAC Relay | 1
Level-4 | Fan Status | 1 | [5 empty] | Mismatch with enable | 60s | Critical |  | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L4-MO-01-UI1 | Level-4 | FCU-L4-MO-01 | Fan Status | FCU-L4-MO-01 | UI1 | MSSB | CCS | 1
Level-4 | SA Temp |  |  | 1 | [7 empty] | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L4-MO-01-UI2 | Level-4 | FCU-L4-MO-01 | SA Temp | FCU-L4-MO-01 | UI2 | SA Ductwork | PDIGR-TE200BE24B2 | 1
Level-4 | Space Temp ( Waiting) |  |  | 1 |  |  |  | >or< Setpoint by 2°C | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L4-MO-01-UI3 | Level-4 | FCU-L4-MO-01 | Space Temp ( Waiting) | FCU-L4-MO-01 | UI3 | Space | PDITE-SENSORX0 | 1
Level-4 | Dirty Filter | 1 | [5 empty] | Change of State | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L4-MO-01-UI4 | Level-4 | FCU-L4-MO-01 | Dirty Filter | FCU-L4-MO-01 | UI4 | Filter Box | AFS - 930.80222524 | 1
Level-4 | Body Hold Temp |  |  | 1 |  |  |  | >or< Setpoint by 2°C | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L4-MO-01-UI5 | Level-4 | FCU-L4-MO-01 | Body Hold Temp | FCU-L4-MO-01 | UI5 | Freezer/Coldroom | PDIGR-TE200BE24B2 | 1
Level-4 | Body Hold Door Reed Sw | 1 | [5 empty] | Door Open to long | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L4-MO-01-UI6 | Level-4 | FCU-L4-MO-01 | Body Hold Door Reed Sw | FCU-L4-MO-01 | UI6 | Freezer/Coldroom | Other
Level-4 | CHW Valve |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L4-MO-01-UO6 | Level-4 | FCU-L4-MO-01 | CHW Valve | FCU-L4-MO-01 | UO6 | FCU | CHWV Actuator | 1
Level-4 | HW Valve |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L4-MO-01-UO7 | Level-4 | FCU-L4-MO-01 | HW Valve | FCU-L4-MO-01 | UO7 | FCU | HHWV Actuator | 1
| Sub Total | 3 | 1 | 3 | 2 | 0 | 1
Mortuary - Autopsy Room
Level-4 | FCU-L4-MO-02 | DI | DO | AI | AO | HLI | Prog | Condition | Timing | Priority | Graphic Name | Functionality | Frequency | [8 empty] | ECB300 | 1
Level-4 | Schedule | [5 empty] | 1 |  |  |  | FCU | Display & Override | 10 Min or > 5% COV |  | FCU-L4-MO-02-SW01 | Level-4 | FCU-L4-MO-02 | Schedule | FCU-L4-MO-02 | SW01 | Software | Software Point | 1
Level-4 | Fan Enable |  | 1 | [8 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L4-MO-02-UO1 | Level-4 | FCU-L4-MO-02 | Fan Enable | FCU-L4-MO-02 | UO1 | MSSB | 12VDC Relay | 1
Level-4 | Fan Status | 1 | [5 empty] | Mismatch with enable | 60s | Critical |  | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L4-MO-02-UI1 | Level-4 | FCU-L4-MO-02 | Fan Status | FCU-L4-MO-02 | UI1 | MSSB | CCS | 1
Level-4 | SA Temp |  |  | 1 | [7 empty] | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L4-MO-02-UI2 | Level-4 | FCU-L4-MO-02 | SA Temp | FCU-L4-MO-02 | UI2 | SA Ductwork | PDIGR-TE200BE24B2 | 1
Level-4 | Spare |  |  | 1 |  |  |  | >or< Setpoint by 2°C | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 11 Min or > 5% COV |  | FCU-L4-MO-02-UI3 | Level-4 | FCU-L4-MO-02 | Spare | FCU-L4-MO-02 | UI3 |  |  | 0
Level-4 | Dirty Filter | 1 | [5 empty] | Change of State | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L4-MO-02-UI4 | Level-4 | FCU-L4-MO-02 | Dirty Filter | FCU-L4-MO-02 | UI4 | Filter Box | AFS - 930.80222524 | 1
Level-4 | Body Hold Refrigeration Unit Status | 1 | [5 empty] | Change of State | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L4-MO-02-UI5 | Level-4 | FCU-L4-MO-02 | Body Hold Refrigeration Unit Status | FCU-L4-MO-02 | UI5 | Filter Box | AFS - 930.80222524 | 1
Level-4 | Body Hold Refrigeration Unit Fault | 1 | [5 empty] | Change of State | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L4-MO-02-UI6 | Level-4 | FCU-L4-MO-02 | Body Hold Refrigeration Unit Fault | FCU-L4-MO-02 | UI6 | Filter Box | AFS - 930.80222524 | 1
Level-4 | Space Temp (Autopsy)/AH | [15 empty] | Cat6 Ethernet Cable | RJ45 Connectors both sides | Space Temp |  | Space | EC - Vue Smart Sensor | 1
Level-4 | Spare |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L4-MO-02-UO5 | Level-4 | FCU-L4-MO-02 | Spare | FCU-L4-MO-02 | UO5 |  |  | 0
Level-4 | CHW Valve |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L4-MO-02-UO6 | Level-4 | FCU-L4-MO-02 | CHW Valve | FCU-L4-MO-02 | UO6 | FCU | CHWV Actuator | 1
Level-4 | HW Valve |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L4-MO-02-UO7 | Level-4 | FCU-L4-MO-02 | HW Valve | FCU-L4-MO-02 | UO7 | FCU | HHWV Actuator | 1
Level-4 | Fan Speed |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L4-MO-02-UO8 | Level-4 | FCU-L4-MO-02 | Fan Speed | FCU-L4-MO-02 | UO8 | FCU | Terminals | 1
| Sub Total | 4 | 1 | 2 | 4 | 0 | 1
Level 4 - Bridge Link
Level-4 | FCU-L4-BR-01 | DI | DO | AI | AO | HLI | Prog | Condition | Timing | Priority | Graphic Name | Functionality | Frequency | [8 empty] | ECB203 | 1
Level-4 | Schedule | [5 empty] | 1 |  |  |  | FCU | Display & Override | 10 Min or > 5% COV |  | FCU-L4-BR-01-SW01 | Level-4 | FCU-L4-BR-01 | Schedule | FCU-L4-BR-01 | SW01 | Software | Software Point | 1
Level-4 | Fan Enable |  | 1 | [8 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L4-BR-01-DO1 | Level-4 | FCU-L4-BR-01 | Fan Enable | FCU-L4-BR-01 | DO1 | MSSB | 24VAC Relay | 1
Level-4 | Fan Status | 1 | [5 empty] | Mismatch with enable | 60s | Critical |  | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L4-BR-01-UI1 | Level-4 | FCU-L4-BR-01 | Fan Status | FCU-L4-BR-01 | UI1 | MSSB | CCS | 1
Level-4 | SA Temp |  |  | 1 | [7 empty] | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L4-BR-01-UI2 | Level-4 | FCU-L4-BR-01 | SA Temp | FCU-L4-BR-01 | UI2 | SA Ductwork | PDIGR-TE200BE24B2 | 1
Level-4 | RA Temp |  |  | 1 |  |  |  | >or< Setpoint by 2°C | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 11 Min or > 5% COV |  | FCU-L4-BR-01-UI3 | Level-4 | FCU-L4-BR-01 | RA Temp | FCU-L4-BR-01 | UI3 | RA Ductwork | PDIGR-TE200BE24B2 | 1
Level-4 | Dirty Filter | 1 | [5 empty] | Change of State | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L4-BR-01-UI4 | Level-4 | FCU-L4-BR-01 | Dirty Filter | FCU-L4-BR-01 | UI4 | Filter Box | AFS - 930.80222524 | 1
Level-4 | CHW Valve |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L4-BR-01-UO6 | Level-4 | FCU-L4-BR-01 | CHW Valve | FCU-L4-BR-01 | UO6 | FCU | CHWV Actuator | 1
Level-4 | HW Valve |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L4-BR-01-UO7 | Level-4 | FCU-L4-BR-01 | HW Valve | FCU-L4-BR-01 | UO7 | FCU | HHWV Actuator | 1
| Sub Total | 2 | 1 | 2 | 2 | 0 | 1
Level 4 - Bridge Link
Level-4 | FCU-L4-BR-02 | DI | DO | AI | AO | HLI | Prog | Condition | Timing | Priority | Graphic Name | Functionality | Frequency | [8 empty] | ECB203 | 1
Level-4 | Schedule | [5 empty] | 1 |  |  |  | FCU | Display & Override | 10 Min or > 5% COV |  | FCU-L4-BR-02-SW01 | Level-4 | FCU-L4-BR-02 | Schedule | FCU-L4-BR-02 | SW01 | Software | Software Point | 1
Level-4 | Fan Enable |  | 1 | [8 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L4-BR-02-DO1 | Level-4 | FCU-L4-BR-02 | Fan Enable | FCU-L4-BR-02 | DO1 | MSSB | 24VAC Relay | 1
Level-4 | Fan Status | 1 | [5 empty] | Mismatch with enable | 60s | Critical |  | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L4-BR-02-UI1 | Level-4 | FCU-L4-BR-02 | Fan Status | FCU-L4-BR-02 | UI1 | MSSB | CCS | 1
Level-4 | SA Temp |  |  | 1 | [7 empty] | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L4-BR-02-UI2 | Level-4 | FCU-L4-BR-02 | SA Temp | FCU-L4-BR-02 | UI2 | SA Ductwork | PDIGR-TE200BE24B2 | 1
Level-4 | RA Temp |  |  | 1 |  |  |  | >or< Setpoint by 2°C | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 11 Min or > 5% COV |  | FCU-L4-BR-02-UI3 | Level-4 | FCU-L4-BR-02 | RA Temp | FCU-L4-BR-02 | UI3 | RA Ductwork | PDIGR-TE200BE24B2 | 1
Level-4 | Dirty Filter | 1 | [5 empty] | Change of State | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L4-BR-02-UI4 | Level-4 | FCU-L4-BR-02 | Dirty Filter | FCU-L4-BR-02 | UI4 | Filter Box | AFS - 930.80222524 | 1
Level-4 | NZ Space Temp |  |  | 1 |  |  |  | >or< Setpoint by 2°C | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | AHU-L4-RN-NZ-UI5 | Level-4 | AHU-L4-RN-NZ | NZ Space Temp | AHU-L4-RN-NZ | UI5 | Space | PDITE-SENSORX0 | 1
Level-4 | CHW Valve |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L4-BR-02-UO6 | Level-4 | FCU-L4-BR-02 | CHW Valve | FCU-L4-BR-02 | UO6 | FCU | CHWV Actuator | 1
Level-4 | HW Valve |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L4-BR-02-UO7 | Level-4 | FCU-L4-BR-02 | HW Valve | FCU-L4-BR-02 | UO7 | FCU | HHWV Actuator | 1
Level-4 | AH LED NZ-RN |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | AH LED NZ-RN |  |  | AH LED NZ-RN | AHU-L4-RN-NZ | UO8 | FCU | PDITE-SENSORX0 | 0
| Sub Total | 2 | 1 | 3 | 3 | 0 | 1
Photo Copy Room
[8 empty] | Alarms |  |  | Graphics |  | History Data
Level 5
Emergency department
Isolation Room
Level-5 | FCU-L5-ISO-01 | DI | DO | AI | AO | HLI | Prog | Condition | Timing | Priority | Graphic Name | Functionality | Frequency | [8 empty] | ECB600 | 1
Level-5 | Fan Enable Low Speed |  | 1 | [7 empty] | FCU Iso | Display & Override | 10 Min or > 5% COV |  | FCU-L5-ISO-01-UO1 | Level-4 | FCU-L5-ISO-01 | Fan Enable Low Speed | FCU-L5-ISO-01 | UO1 | MSSB | 12VDC Relay | 1
Level-5 | Fan Enable Medium Speed |  | 1 | [8 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L5-ISO-01-UO2 | Level-4 | FCU-L5-ISO-01 | Fan Enable Medium Speed | FCU-L5-ISO-01 | UO2 | MSSB | 12VDC Relay | 1
Level-5 | Fan Enable High Speed |  | 1 | [8 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L5-ISO-01-UO3 | Level-4 | FCU-L5-ISO-01 | Fan Enable High Speed | FCU-L5-ISO-01 | UO3 | MSSB | 12VDC Relay | 1
Level-5 | SA Fan Status | 1 | [5 empty] | Mismatch with enable | 60s | Critical |  | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L5-ISO-01-UI1 | Level 5 | FCU-L5-ISO-01 | SA Fan Status | FCU-L5-ISO-01 | UI1 | MSSB | AFS - 930.80222524 | 1
Level-5 | SA Temp |  |  | 1 | [7 empty] | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L5-ISO-01-UI2 | Level 5 | FCU-L5-ISO-01 | SA Temp | FCU-L5-ISO-01 | UI2 | SA Ductwork | PDIGR-TE200BE24B2 | 1
Level-5 | Space Temp |  |  | 1 |  |  |  | >or< Setpoint by 2°C | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L5-ISO-01-UI3 | Level 5 | FCU-L5-ISO-01 | Space Temp | FCU-L5-ISO-01 | UI3 | Space | PDITE-SENSORX0 | 1
Level-5 | Velocity |  |  | 1 |  |  |  | >or< Setpoint by 10l/s | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L5-ISO-01-UI4 | Level 5 | FCU-L5-ISO-01 | Velocity | FCU-L5-ISO-01 | UI4 | SA Velocity | QVM62.1 | 1
Level-5 | RA Humidity |  |  | 1 |  |  |  | >or< Setpoint by 5% | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L5-ISO-01-UI5 | Level 5 | FCU-L5-ISO-01 | RA Humidity | FCU-L5-ISO-01 | UI5 | RA Ductwork | QFM2160 Humidity | 1
Level-5 | Dirty SA Pre-Filter | 1 | [5 empty] | Change of State | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L5-ISO-01-UI6 | Level 5 | FCU-L5-ISO-01 | Dirty SA Pre-Filter | FCU-L5-ISO-01 | UI6 | Filter Box | AFS - 930.80222524 | 1
Level-5 | Dirty SA Deep Bed Filter | 1 | [5 empty] | Change of State | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L5-ISO-01-UI7 | Level 5 | FCU-L5-ISO-01 | Dirty SA Deep Bed Filter | FCU-L5-ISO-01 | UI7 | Filter Box | AFS - 930.80222524 | 1
Level-5 | EA ISO Rm Heppa Filter Diff Press |  |  | 1 |  |  |  | >or< Setpoint by 5Pa | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L5-ISO-01-UI8 | Level 5 | FCU-L5-ISO-01 | EA ISO Rm Heppa Filter Diff Press | FCU-L5-ISO-01 | UI8 | Filter Press | QBM2030-5 | 1
Level-5 | EA ISO Toilet Heppa Filter Diff Press |  |  | 1 |  |  |  | >or< Setpoint by 5Pa | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L5-ISO-01-UI9 | Level 5 | FCU-L5-ISO-01 | EA ISO Toilet Heppa Filter Diff Press | FCU-L5-ISO-01 | UI9 | Filter Press | QBM2030-5 | 1
Level-5 | ISO Rm Diff Press |  |  | 1 |  |  |  | >or< Setpoint by 5Pa | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L5-ISO-01-UI10 | Level 5 | FCU-L5-ISO-01 | ISO Rm Diff Press | FCU-L5-ISO-01 | UI10 | Room DP | QBM2030-1U | 1
Level-5 | Anteroom Diff Press |  |  | 1 |  |  |  | >or< Setpoint by 5Pa | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L5-ISO-01-UI11 | Level 5 | FCU-L5-ISO-01 | Anteroom Diff Press | FCU-L5-ISO-01 | UI11 | Room DP | QBM2030-1U | 1
Level-5 | NZ Space Temp |  |  | 1 |  |  |  | >or< Setpoint by 2°C | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | AHU-L5-ED-2-NZ-UI12 | Level 5 | AHU-L5-ED-2-NZ | NZ Space Temp | AHU-L5-ED-2-NZ | UI12 | Space | PDITE-SENSORX0 | 1
Level-5 | Pressure Monitor | [15 empty] | Cat6 Ethernet Cable | RJ45 Connectors both sides | Pressure Monitor |  | Space | EC - Vue Smart Sensor | 1
Level-5 | CHW Valve |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L5-ISO-01-UO4 | Level 5 | FCU-L5-ISO-01 | CHW Valve | FCU-L5-ISO-01 | UO4 | FCU | CHWV Actuator | 1
Level-5 | HW Valve |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L5-ISO-01-UO5 | Level 5 | FCU-L5-ISO-01 | HW Valve | FCU-L5-ISO-01 | UO5 | FCU | HHWV Actuator | 1
Level-5 | Supply Damper |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L5-ISO-01-UO6 | Level 5 | FCU-L5-ISO-01 | Supply Damper | FCU-L5-ISO-01 | UO6 | FCU | GDB161.1E | 1
Level-5 | ISO Rm Audio Alarm |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L5-ISO-01-UO7 | Level 5 | FCU-L5-ISO-01 | ISO Rm Audio Alarm | FCU-L5-ISO-01 | UO7 | FCU | 12VDC Relay | 1
Level-5 | Anteroom Audio Alarm |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L5-ISO-01-UO8 | Level 5 | FCU-L5-ISO-01 | Anteroom Audio Alarm | FCU-L5-ISO-01 | UO8 | FCU | 12VDC Relay | 1
Level-5 | OAF-L5-02 Fan Enable |  | 1 | [8 empty] | Display & Override | 10 Min or > 5% COV |  | OAF-L5-02-UO9 | Level 5 | OAF-L5-02 | OAF-L5-02 Fan Enable | OAF-L5-02 | UO9 | MSSB | 12VDC Relay | 1
Level-5 | AH LED NZ-ED-2 |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | AHU-L5-ED-2-NZ-UO10 | Level 5 | AHU-L5-ED-2-NZ | AH LED NZ-ED-2 | AHU-L5-ED-2-NZ | UO10 | FCU | PDITE-SENSORX0 | 0
| Sub Total | 3 | 4 | 9 | 6 | 0 | 0
Isolation Room
Level-5 | FCU-L5-ISO-02 | DI | DO | AI | AO | HLI | Prog | Condition | Timing | Priority | Graphic Name | Functionality | Frequency | [8 empty] | ECB600 | 1
Level-5 | Fan Enable Low Speed |  | 1 | [8 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L4-BR-02-UO1 | Level-4 | FCU-L4-BR-02 | Fan Enable Low Speed | FCU-L4-BR-02 | UO1 | MSSB | 24VAC Relay | 1
Level-5 | Fan Enable Medium Speed |  | 1 | [8 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L4-BR-02-UO2 | Level-4 | FCU-L4-BR-02 | Fan Enable Medium Speed | FCU-L4-BR-02 | UO2 | MSSB | 24VAC Relay | 1
Level-5 | Fan Enable High Speed |  | 1 | [8 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L4-BR-02-UO3 | Level-4 | FCU-L4-BR-02 | Fan Enable High Speed | FCU-L4-BR-02 | UO3 | MSSB | 24VAC Relay | 1
Level-5 | SA Fan Status | 1 | [5 empty] | Mismatch with enable | 60s | Critical |  | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L5-ISO-01-UI1 | Level 5 | FCU-L5-ISO-01 | SA Fan Status | FCU-L5-ISO-01 | UI1 | MSSB | AFS - 930.80222524 | 1
Level-5 | SA Temp |  |  | 1 | [7 empty] | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L5-ISO-01-UI2 | Level 5 | FCU-L5-ISO-01 | SA Temp | FCU-L5-ISO-01 | UI2 | SA Ductwork | PDIGR-TE200BE24B2 | 1
Level-5 | Space Temp |  |  | 1 |  |  |  | >or< Setpoint by 2°C | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L5-ISO-01-UI3 | Level 5 | FCU-L5-ISO-01 | Space Temp | FCU-L5-ISO-01 | UI3 | Space | PDITE-SENSORX0 | 1
Level-5 | Velocity |  |  | 1 |  |  |  | >or< Setpoint by 10l/s | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L5-ISO-01-UI4 | Level 5 | FCU-L5-ISO-01 | Velocity | FCU-L5-ISO-01 | UI4 | SA Velocity | QVM62.1 | 1
Level-5 | RA Humidity |  |  | 1 |  |  |  | >or< Setpoint by 5% | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L5-ISO-01-UI5 | Level 5 | FCU-L5-ISO-01 | RA Humidity | FCU-L5-ISO-01 | UI5 | RA Ductwork | QFM2160 Humidity | 1
Level-5 | Dirty SA Pre-Filter | 1 | [5 empty] | Change of State | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L5-ISO-01-UI6 | Level 5 | FCU-L5-ISO-01 | Dirty SA Pre-Filter | FCU-L5-ISO-01 | UI6 | Filter Box | AFS - 930.80222524 | 1
Level-5 | Dirty SA Deep Bed Filter | 1 | [5 empty] | Change of State | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L5-ISO-01-UI7 | Level 5 | FCU-L5-ISO-01 | Dirty SA Deep Bed Filter | FCU-L5-ISO-01 | UI7 | Filter Box | AFS - 930.80222524 | 1
Level-5 | EA ISO Rm Heppa Filter Diff Press |  |  | 1 |  |  |  | >or< Setpoint by 5Pa | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L5-ISO-01-UI8 | Level 5 | FCU-L5-ISO-01 | EA ISO Rm Heppa Filter Diff Press | FCU-L5-ISO-01 | UI8 | Filter Press | QBM2030-5 | 1
Level-5 | EA ISO Toilet Heppa Filter Diff Press |  |  | 1 |  |  |  | >or< Setpoint by 5Pa | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L5-ISO-01-UI9 | Level 5 | FCU-L5-ISO-01 | EA ISO Toilet Heppa Filter Diff Press | FCU-L5-ISO-01 | UI9 | Filter Press | QBM2030-5 | 1
Level-5 | ISO Rm Diff Press |  |  | 1 |  |  |  | >or< Setpoint by 5Pa | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L5-ISO-01-UI10 | Level 5 | FCU-L5-ISO-01 | ISO Rm Diff Press | FCU-L5-ISO-01 | UI10 | Room DP | QBM2030-1U | 1
Level-5 | Anteroom Diff Press |  |  | 1 |  |  |  | >or< Setpoint by 5Pa | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L5-ISO-01-UI11 | Level 5 | FCU-L5-ISO-01 | Anteroom Diff Press | FCU-L5-ISO-01 | UI11 | Room DP | QBM2030-1U | 1
Level-5 | EZ Space Temp |  |  | 1 |  |  |  | >or< Setpoint by 2°C | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | AHU-L5-ED2-EZ-UI12 | Level 5 | AHU-L5-ED2-EZ | EZ Space Temp | AHU-L5-ED2-EZ | UI12 | Space | PDITE-SENSORX0 | 1
Level-5 | Pressure Monitor | [15 empty] | Cat6 Ethernet Cable | RJ45 Connectors both sides | Pressure Monitor |  | Space | EC - Vue Smart Sensor | 1
Level-5 | CHW Valve |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L5-ISO-01-UO4 | Level 5 | FCU-L5-ISO-01 | CHW Valve | FCU-L5-ISO-01 | UO4 | FCU | CHWV Actuator | 1
Level-5 | HW Valve |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L5-ISO-01-UO5 | Level 5 | FCU-L5-ISO-01 | HW Valve | FCU-L5-ISO-01 | UO5 | FCU | HHWV Actuator | 1
Level-5 | Supply Damper |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L5-ISO-01-UO6 | Level 5 | FCU-L5-ISO-01 | Supply Damper | FCU-L5-ISO-01 | UO6 | FCU | GDB161.1E | 1
Level-5 | ISO Rm Audio Alarm |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L5-ISO-01-UO7 | Level 5 | FCU-L5-ISO-01 | ISO Rm Audio Alarm | FCU-L5-ISO-01 | UO7 | FCU | 12VDC Relay | 1
Level-5 | Anteroom Audio Alarm |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L5-ISO-01-UO8 | Level 5 | FCU-L5-ISO-01 | Anteroom Audio Alarm | FCU-L5-ISO-01 | UO8 | FCU | 12VDC Relay | 1
Level-5 | AH LED EZ-ED-2 |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | AHU-L5-ED2-EZ-UO10 | Level 5 | AHU-L5-ED2-EZ | AH LED EZ-ED-2 | AHU-L5-ED2-EZ | UO10 | FCU | PDITE-SENSORX0 | 0
| Sub Total | 3 | 3 | 9 | 6 | 0 | 0
Comms Rooms 5108
Level-5 | FCU-L5-01 | DI | DO | AI | AO | HLI | Prog | Condition | Timing | Priority | Graphic Name | Functionality | Frequency | [8 empty] | ECB203 | 1
Level-5 | Schedule | [5 empty] | 1 |  |  |  | FCU Iso | Display & Override | 10 Min or > 5% COV |  | FCU-L5-01-SW01 | Level 5 | FCU-L5-01 | Schedule | FCU-L5-01 | SW01 | Software | Software Point | 1
Level-5 | Fan Enable |  | 1 | [8 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L5-01-DO1 | Level 5 | FCU-L5-01 | Fan Enable | FCU-L5-01 | DO1 | MSSB | 24VAC Relay | 1
Level-5 | Fan Status | 1 | [5 empty] | Mismatch with enable | 60s | Critical |  | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L5-01-UI1 | Level 5 | FCU-L5-01 | Fan Status | FCU-L5-01 | UI1 | MSSB | CCS | 1
Level-5 | SA Temp |  |  | 1 | [7 empty] | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L5-01-UI2 | Level 5 | FCU-L5-01 | SA Temp | FCU-L5-01 | UI2 | SA Ductwork | PDIGR-TE200BE24B2 | 1
Level-5 | Space Temp |  |  | 1 |  |  |  | >or< Setpoint by 2°C | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L5-01-UI3 | Level 5 | FCU-L5-01 | Space Temp | FCU-L5-01 | UI3 | Space | PDITE-SENSORX0 | 1
Level-5 | Dirty Filter | 1 | [5 empty] | Change of State | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L5-01-UI4 | Level 5 | FCU-L5-01 | Dirty Filter | FCU-L5-01 | UI4 | Filter Box | AFS - 930.80222524 | 1
Level-5 | Blood Fridge Fridge Temp (Rm 5063 Bay Pathology) |  |  | 1 | [7 empty] | Display / Red on Alarm | 10 Min or > 5% COV |  | Fridges-UI5 | Level 5 | Fridges | Blood Fridge Fridge Temp (Rm 5063 Bay Pathology) | Fridges | UI5 | Space | PDIGR-TE200BE24B2 | 1
Level-5 | Blood Fridge Fridge Fault (Rm 5063 Bay Pathology) | 1 | [5 empty] | Change of State | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | Fridges-UI6 | Level 5 | Fridges | Blood Fridge Fridge Fault (Rm 5063 Bay Pathology) | Fridges | UI6 | Space | Terminals | 1
Level-5 | CHW Valve |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L5-01-UO6 | Level 5 | FCU-L5-01 | CHW Valve | FCU-L5-01 | UO6 | FCU | CHWV Actuator | 1
Level-5 | Fan Speed |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L5-01-UO8 | Level 5 | FCU-L5-01 | Fan Speed | FCU-L5-01 | UO8 | FCU | Terminals | 1
| Sub Total | 3 | 1 | 3 | 2 | 0 | 1
Lift Lobby and Corridor Areas
Level-5 | FCU-L5-02 | DI | DO | AI | AO | HLI | Prog | Condition | Timing | Priority | Graphic Name | Functionality | Frequency | [8 empty] | ECB203 | 1
Level-5 | Schedule | [5 empty] | 1 |  |  |  | FCU Iso | Display & Override | 10 Min or > 5% COV |  | FCU-L5-02-SW01 | Level 5 | FCU-L5-02 | Schedule | FCU-L5-02 | SW01 | Software | Software Point | 1
Level-5 | Fan Enable |  | 1 | [8 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L5-02-DO1 | Level 5 | FCU-L5-02 | Fan Enable | FCU-L5-02 | DO1 | MSSB | 24VAC Relay | 1
Level-5 | OAF-L5-01 Fan Enable |  | 1 | [8 empty] | Display & Override | 10 Min or > 5% COV |  | OAF-L5-01-DO2 | Level 5 | OAF-L5-01 | OAF-L5-01 Fan Enable | OAF-L5-01 | DO2 | MSSB | 24VAC Relay | 1
Level-5 | OAF-L5-02 Fan Enable |  | 1 | [8 empty] | Display & Override | 10 Min or > 5% COV |  | OAF-L5-02-DO3 | Level 5 | OAF-L5-02 | OAF-L5-02 Fan Enable | OAF-L5-02 | DO3 | MSSB | 24VAC Relay | 1
Level-5 | Fan Status | 1 | [5 empty] | Mismatch with enable | 60s | Critical |  | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L5-02-UI1 | Level 5 | FCU-L5-02 | Fan Status | FCU-L5-02 | UI1 | MSSB | CCS | 1
Level-5 | SA Temp |  |  | 1 | [7 empty] | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L5-02-UI2 | Level 5 | FCU-L5-02 | SA Temp | FCU-L5-02 | UI2 | SA Ductwork | PDIGR-TE200BE24B2 | 1
Level-5 | RA Temp |  |  | 1 |  |  |  | >or< Setpoint by 2°C | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L5-02-UI3 | Level 5 | FCU-L5-02 | RA Temp | FCU-L5-02 | UI3 | RA Ductwork | PDIGR-TE200BE24B2 | 1
Level-5 | Dirty Filter | 1 | [5 empty] | Change of State | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L5-02-UI4 | Level 5 | FCU-L5-02 | Dirty Filter | FCU-L5-02 | UI4 | Filter Box | AFS - 930.80222524 | 1
Level-5 | OAF-L5-01 Status | 1 | [12 empty] | OAF-L5-01-UI5 | Level 5 | OAF-L5-01 | OAF-L5-01 Status | OAF-L5-01 | UI5 | MSSB | CCS | 1
Level-5 | OAF-L5-02 Status | 1 | [12 empty] | OAF-L5-02-UI6 | Level 5 | OAF-L5-02 | OAF-L5-02 Status | OAF-L5-02 | UI6 | MSSB | CCS | 1
Level-5 | CHW Valve |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L5-02-UO6 | Level 5 | FCU-L5-02 | CHW Valve | FCU-L5-02 | UO6 | FCU | CHWV Actuator | 1
Level-5 | HW Valve |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L5-02-UO7 | Level 5 | FCU-L5-02 | HW Valve | FCU-L5-02 | UO7 | FCU | HHWV Actuator | 1
| Sub Total | 4 | 3 | 2 | 2 | 0 | 1
Lift Lobby and Corridor Areas
Level-5 | FCU-L5-03 | DI | DO | AI | AO | HLI | Prog | Condition | Timing | Priority | Graphic Name | Functionality | Frequency | [8 empty] | ECB203 | 1
Level-5 | Schedule | [5 empty] | 1 |  |  |  | FCU Iso | Display & Override | 10 Min or > 5% COV |  | FCU-L5-03-SW01 | Level 5 | FCU-L5-03 | Schedule | FCU-L5-03 | SW01 | Software | Software Point | 1
Level-5 | Fan Enable |  | 1 | [8 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L5-03-DO1 | Level 5 | FCU-L5-03 | Fan Enable | FCU-L5-03 | DO1 | MSSB | 24VAC Relay | 1
Level-5 | Fan Status | 1 | [5 empty] | Mismatch with enable | 60s | Critical |  | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L5-03-UI1 | Level 5 | FCU-L5-03 | Fan Status | FCU-L5-03 | UI1 | MSSB | CCS | 1
Level-5 | SA Temp |  |  | 1 | [7 empty] | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L5-03-UI2 | Level 5 | FCU-L5-03 | SA Temp | FCU-L5-03 | UI2 | SA Ductwork | PDIGR-TE200BE24B2 | 1
Level-5 | RA Temp |  |  | 1 |  |  |  | >or< Setpoint by 2°C | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L5-03-UI3 | Level 5 | FCU-L5-03 | RA Temp | FCU-L5-03 | UI3 | RA Ductwork | PDIGR-TE200BE24B2 | 1
Level-5 | Dirty Filter | 1 | [5 empty] | Change of State | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L5-03-UI4 | Level 5 | FCU-L5-03 | Dirty Filter | FCU-L5-03 | UI4 | Filter Box | AFS - 930.80222524 | 1
Level-5 | Fire | 1 | [5 empty] | COS | 0s | Fire |  | Display / Red on Alarm | 10 Min or > 5% COV |  | L5 Fire-UI5 | Level-6 | FCU-L5-03 | Fire | L5 Fire | UI5 | MSSB | 24VAC Relay | 1
Level-5 | CHW Valve |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L5-03-UO6 | Level 5 | FCU-L5-03 | CHW Valve | FCU-L5-03 | UO6 | FCU | CHWV Actuator | 1
Level-5 | HW Valve |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L5-03-UO7 | Level 5 | FCU-L5-03 | HW Valve | FCU-L5-03 | UO7 | FCU | HHWV Actuator | 1
| Sub Total | 3 | 1 | 2 | 2 | 0 | 1
Level 5 - Bridge Link
Level-5 | FCU-L5-BR-01 | DI | DO | AI | AO | HLI | Prog | Condition | Timing | Priority | Graphic Name | Functionality | Frequency | [8 empty] | ECB203 | 1
Level-5 | Schedule | [5 empty] | 1 |  |  |  | FCU Iso | Display & Override | 10 Min or > 5% COV |  | FCU-L5-BR-01-SW01 | Level 5 | FCU-L5-BR-01 | Schedule | FCU-L5-BR-01 | SW01 | Software | Software Point | 1
Level-5 | Fan Enable |  | 1 | [8 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L5-BR-01-DO1 | Level 5 | FCU-L5-BR-01 | Fan Enable | FCU-L5-BR-01 | DO1 | MSSB | 24VAC Relay | 1
Level-5 | Fan Status | 1 | [5 empty] | Mismatch with enable | 60s | Critical |  | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L5-BR-01-UI1 | Level 5 | FCU-L5-BR-01 | Fan Status | FCU-L5-BR-01 | UI1 | MSSB | CCS | 1
Level-5 | SA Temp |  |  | 1 | [7 empty] | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L5-BR-01-UI2 | Level 5 | FCU-L5-BR-01 | SA Temp | FCU-L5-BR-01 | UI2 | SA Ductwork | PDIGR-TE200BE24B2 | 1
Level-5 | RA Temp |  |  | 1 |  |  |  | >or< Setpoint by 2°C | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L5-BR-01-UI3 | Level 5 | FCU-L5-BR-01 | RA Temp | FCU-L5-BR-01 | UI3 | RA Ductwork | PDIGR-TE200BE24B2 | 1
Level-5 | Dirty Filter | 1 | [5 empty] | Change of State | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L5-BR-01-UI4 | Level 5 | FCU-L5-BR-01 | Dirty Filter | FCU-L5-BR-01 | UI4 | Filter Box | AFS - 930.80222524 | 1
Level-5 | CHW Valve |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L5-BR-01-UO6 | Level 5 | FCU-L5-BR-01 | CHW Valve | FCU-L5-BR-01 | UO6 | FCU | CHWV Actuator | 1
Level-5 | HW Valve |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L5-BR-01-UO7 | Level 5 | FCU-L5-BR-01 | HW Valve | FCU-L5-BR-01 | UO7 | FCU | HHWV Actuator | 1
| Sub Total | 2 | 1 | 2 | 2 | 0 | 1
Level 5 - Bridge Link
Level-5 | FCU-L5-BR-02 | DI | DO | AI | AO | HLI | Prog | Condition | Timing | Priority | Graphic Name | Functionality | Frequency | [8 empty] | ECB203 | 1
Level-5 | Schedule | [5 empty] | 1 |  |  |  | FCU Iso | Display & Override | 10 Min or > 5% COV |  | FCU-L5-BR-02-SW01 | Level 5 | FCU-L5-BR-02 | Schedule | FCU-L5-BR-02 | SW01 | Software | Software Point | 1
Level-5 | Fan Enable |  | 1 | [8 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L5-BR-02-DO1 | Level 5 | FCU-L5-BR-02 | Fan Enable | FCU-L5-BR-02 | DO1 | MSSB | 24VAC Relay | 1
Level-5 | Fan Status | 1 | [5 empty] | Mismatch with enable | 60s | Critical |  | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L5-BR-02-UI1 | Level 5 | FCU-L5-BR-02 | Fan Status | FCU-L5-BR-02 | UI1 | MSSB | CCS | 1
Level-5 | SA Temp |  |  | 1 | [7 empty] | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L5-BR-02-UI2 | Level 5 | FCU-L5-BR-02 | SA Temp | FCU-L5-BR-02 | UI2 | SA Ductwork | PDIGR-TE200BE24B2 | 1
Level-5 | RA Temp |  |  | 1 |  |  |  | >or< Setpoint by 2°C | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L5-BR-02-UI3 | Level 5 | FCU-L5-BR-02 | RA Temp | FCU-L5-BR-02 | UI3 | RA Ductwork | PDIGR-TE200BE24B2 | 1
Level-5 | Dirty Filter | 1 | [5 empty] | Change of State | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L5-BR-02-UI4 | Level 5 | FCU-L5-BR-02 | Dirty Filter | FCU-L5-BR-02 | UI4 | Filter Box | AFS - 930.80222524 | 1
Level-5 | [15 empty] | Level 5 |  |  |  | UI5
Level-5 | - | [14 empty] | Level 5 |  | - |  | UI6 |  | -
Level-5 | CHW Valve |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L5-BR-02-UO6 | Level 5 | FCU-L5-BR-02 | CHW Valve | FCU-L5-BR-02 | UO6 | FCU | CHWV Actuator | 1
Level-5 | HW Valve |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L5-BR-02-UO7 | Level 5 | FCU-L5-BR-02 | HW Valve | FCU-L5-BR-02 | UO7 | FCU | HHWV Actuator | 1
| Sub Total | 2 | 1 | 2 | 2 | 0 | 1
Emergency Department - Consulting Rooms
Level-5 | FCU-L5-ED-01 | DI | DO | AI | AO | HLI | Prog | Condition | Timing | Priority | Graphic Name | Functionality | Frequency | [8 empty] | ECB300 | 1
Level-5 | Schedule | [5 empty] | 1 |  |  |  | FCU Iso | Display & Override | 10 Min or > 5% COV |  | FCU-L5-ED-01-SW01 | Level 5 | FCU-L5-ED-01 | Schedule | FCU-L5-ED-01 | SW01 | Software | Software Point | 1
Level-5 | Fan Enable |  | 1 | [8 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L5-ED-01-UO1 | Level 5 | FCU-L5-ED-01 | Fan Enable | FCU-L5-ED-01 | UO1 | MSSB | 12VDC Relay | 1
Level-5 | Fan Status | 1 | [5 empty] | Mismatch with enable | 60s | Critical |  | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L5-ED-01-UI1 | Level 5 | FCU-L5-ED-01 | Fan Status | FCU-L5-ED-01 | UI1 | MSSB | CCS | 1
Level-5 | SA Temp |  |  | 1 | [7 empty] | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L5-ED-01-UI2 | Level 5 | FCU-L5-ED-01 | SA Temp | FCU-L5-ED-01 | UI2 | SA Ductwork | PDIGR-TE200BE24B2 | 1
Level-5 | Spare |  |  | 1 |  |  |  | >or< Setpoint by 2°C | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L5-ED-01-UI3 | Level 5 | FCU-L5-ED-01 | Spare | FCU-L5-ED-01 | UI3 | Space
Level-5 | Dirty Filter | 1 | [5 empty] | Change of State | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L5-ED-01-UI4 | Level 5 | FCU-L5-ED-01 | Dirty Filter | FCU-L5-ED-01 | UI4 | Filter Box | AFS - 930.80222524 | 1
Level-5 | NZ Space Temp |  |  | 1 |  |  |  | >or< Setpoint by 2°C | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | AHU-L5-ED1-NZ-UI5 | Level 5 | AHU-L5-ED1-NZ | NZ Space Temp | AHU-L5-ED1-NZ | UI5 | Space | PDITE-SENSORX0 | 1
Level-5 | SZ Space Temp |  |  | 1 |  |  |  | >or< Setpoint by 2°C | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | AHU-L5-ED1-SZ-UI6 | Level 5 | AHU-L5-ED1-SZ | SZ Space Temp | AHU-L5-ED1-SZ | UI6 | Space | PDITE-SENSORX0 | 1
Level-5 | Small Drug Fridge Temp (Rm 5054 Clean Utility) |  |  | 1 | [7 empty] | Display / Red on Alarm | 10 Min or > 5% COV |  | Fridges-UI7 | Level 5 | Fridges | Small Drug Fridge Temp (Rm 5054 Clean Utility) | Fridges | UI7 | Space | PDIGR-TE200BE24B2 | 1
Level-5 | Small Drug Fridge Fault (Rm 5054 Clean Utility) | 1 | [5 empty] | Change of State | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | Fridges-UI8 | Level 5 | Fridges | Small Drug Fridge Fault (Rm 5054 Clean Utility) | Fridges | UI8 | Space | Terminals | 1
Level-5 | Small Drug Fridge Temp (Rm 5218 Consulting) |  |  | 1 | [7 empty] | Display / Red on Alarm | 10 Min or > 5% COV |  | Fridges-UI9 | Level 5 | Fridges | Small Drug Fridge Temp (Rm 5218 Consulting) | Fridges | UI9 | Space | PDIGR-TE200BE24B2 | 1
Level-5 | Small Drug Fridge Fault (Rm 5218 Consulting) | 1 | [5 empty] | Change of State | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | Fridges-UI10 | Level 5 | Fridges | Small Drug Fridge Fault (Rm 5218 Consulting) | Fridges | UI10 | Space | Terminals | 1
Level-5 | Space Temp (Consult Rm 5022) | [15 empty] | Cat6 Ethernet Cable | RJ45 Connectors both sides | Space Temp |  | Space | EC - Vue Smart Sensor | 1
Level-5 | AH LED NZ-ED-1 |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | AHU-L5-ED-1-NZ-UO4 | Level 5 | AHU-L5-ED-1-NZ | AH LED NZ-ED-1 | AHU-L5-ED-1-NZ | UO4 | FCU | PDITE-SENSORX0 | 0
Level-5 | AH LED SZ-ED-1 |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | AHU-L5-ED-1-SZ-UO5 | Level 5 | AHU-L5-ED-1-SZ | AH LED SZ-ED-1 | AHU-L5-ED-1-SZ | UO5 | FCU | PDITE-SENSORX0 | 0
Level-5 | CHW Valve |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L5-ED-01-UO6 | Level 5 | FCU-L5-ED-01 | CHW Valve | FCU-L5-ED-01 | UO6 | FCU | CHWV Actuator | 1
Level-5 | HW Valve |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L5-ED-01-UO7 | Level 5 | FCU-L5-ED-01 | HW Valve | FCU-L5-ED-01 | UO7 | FCU | HHWV Actuator | 1
| Sub Total | 4 | 1 | 6 | 4 | 0 | 1
Emergency Department – Main Waiting Room
Level-5 | FCU-L5-ED-02 | DI | DO | AI | AO | HLI | Prog | Condition | Timing | Priority | Graphic Name | Functionality | Frequency | [8 empty] | ECB300 | 1
Level-5 | Schedule | [5 empty] | 1 |  |  |  | FCU Iso | Display & Override | 10 Min or > 5% COV |  | FCU-L5-ED-02-SW01 | Level 5 | FCU-L5-ED-02 | Schedule | FCU-L5-ED-02 | SW01 | Software | Software Point | 1
Level-5 | Fan Enable |  | 1 | [8 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L5-ED-02-UO1 | Level 5 | FCU-L5-ED-02 | Fan Enable | FCU-L5-ED-02 | UO1 | MSSB | 12VDC Relay | 1
Level-5 | Fan Status | 1 | [5 empty] | Mismatch with enable | 60s | Critical |  | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L5-ED-02-UI1 | Level 5 | FCU-L5-ED-02 | Fan Status | FCU-L5-ED-02 | UI1 | MSSB | CCS | 1
Level-5 | SA Temp |  |  | 1 | [7 empty] | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L5-ED-02-UI2 | Level 5 | FCU-L5-ED-02 | SA Temp | FCU-L5-ED-02 | UI2 | SA Ductwork | PDIGR-TE200BE24B2 | 1
Level-5 | Spare |  |  | 1 |  |  |  | >or< Setpoint by 2°C | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L5-ED-02-UI3 | Level 5 | FCU-L5-ED-02 | Spare | FCU-L5-ED-02 | UI3 | Space
Level-5 | Dirty Filter | 1 | [5 empty] | Change of State | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L5-ED-02-UI4 | Level 5 | FCU-L5-ED-02 | Dirty Filter | FCU-L5-ED-02 | UI4 | Filter Box | AFS - 930.80222524 | 1
Level-5 | WZ Space Temp |  |  | 1 |  |  |  | >or< Setpoint by 2°C | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | AHU-L5-ED-1-WZ-UI5 | Level 5 | AHU-L5-ED-1-WZ | WZ Space Temp | AHU-L5-ED-1-WZ | UI5 | Space | PDITE-SENSORX0 | 1
Level-5 | Space Temp (Waiting 5003) | [15 empty] | Cat6 Ethernet Cable | RJ45 Connectors both sides | Space Temp |  | Space | EC - Vue Smart Sensor | 1
Level-5 | Spare |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L5-ED-02-UO3 | Level 5 | FCU-L5-ED-02 | Spare | FCU-L5-ED-02 | UO3 | FCU | PDITE-SENSORX0 | 0
Level-5 | AH LED WZ-ED-1 |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | AHU-L5-ED1-WZ-UO4 | Level 5 | AHU-L5-ED1-WZ | AH LED WZ-ED-1 | AHU-L5-ED1-WZ | UO4 | FCU | PDITE-SENSORX0 | 0
Level-5 | Spare |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L5-ED-02-UO5 | Level 5 | FCU-L5-ED-02 | Spare | FCU-L5-ED-02 | UO5 | FCU
Level-5 | CHW Valve |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L5-ED-02-UO6 | Level 5 | FCU-L5-ED-02 | CHW Valve | FCU-L5-ED-02 | UO6 | FCU | CHWV Actuator | 1
Level-5 | HW Valve |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L5-ED-02-UO7 | Level 5 | FCU-L5-ED-02 | HW Valve | FCU-L5-ED-02 | UO7 | FCU | HHWV Actuator | 1
Level-5 | Fan Speed |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L5-ED-02-UO8 | Level 5 | FCU-L5-ED-02 | Fan Speed | FCU-L5-ED-02 | UO8 | FCU | Terminals | 1
| Sub Total | 2 | 1 | 3 | 6 | 0 | 1
Radiology – X-ray Rooms
Level-5 | FCU-L5-RD-01 | DI | DO | AI | AO | HLI | Prog | Condition | Timing | Priority | Graphic Name | Functionality | Frequency | [8 empty] | ECB400 | 1
Level-5 | Schedule | [5 empty] | 1 |  |  |  | FCU Iso | Display & Override | 10 Min or > 5% COV |  | FCU-L5-RD-01-SW01 | Level 5 | FCU-L5-RD-01 | Schedule | FCU-L5-RD-01 | SW01 | Software | Software Point | 1
Level-5 | Fan Enable |  | 1 | [8 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L5-RD-01-UO1 | Level 5 | FCU-L5-RD-01 | Fan Enable | FCU-L5-RD-01 | UO1 | MSSB | 12VDC Relay | 1
Level-5 | Fan Status | 1 | [5 empty] | Mismatch with enable | 60s | Critical |  | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L5-RD-01-UI1 | Level 5 | FCU-L5-RD-01 | Fan Status | FCU-L5-RD-01 | UI1 | MSSB | AFS - 930.80222524 | 1
Level-5 | SA Temp |  |  | 1 | [7 empty] | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L5-RD-01-UI2 | Level 5 | FCU-L5-RD-01 | SA Temp | FCU-L5-RD-01 | UI2 | SA Ductwork | PDIGR-TE200BE24B2 | 1
Level-5 | Spare |  |  | 1 |  |  |  | >or< Setpoint by 2°C | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L5-RD-01-UI3 | Level 5 | FCU-L5-RD-01 | Spare | FCU-L5-RD-01 | UI3 | Space
Level-5 | Space Temp 2 |  |  | 1 | [7 empty] | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L5-RD-01-UI4 | Level 5 | FCU-L5-RD-01 | Space Temp 2 | FCU-L5-RD-01 | UI4 | Space | PDITE-SENSORX0 | 1
Level-5 | Space Temp 3 | 1 | [5 empty] | Change of State | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L5-RD-01-UI5 | Level 5 | FCU-L5-RD-01 | Space Temp 3 | FCU-L5-RD-01 | UI5 | Filter Box | PDITE-SENSORX0 | 1
Level-5 | Dirty Filter | [13 empty] | FCU-L5-RD-01-UI6 | Level 5 | FCU-L5-RD-01 | Dirty Filter | FCU-L5-RD-01 | UI6 | Filter Box | AFS - 930.80222524 | 1
Level-5 | Small Drug Fridge Temp (Rm 5198 Clean Utility) |  |  | 1 | [7 empty] | Display / Red on Alarm | 10 Min or > 5% COV |  | Fridges-UI7 | Level 5 | Fridges | Small Drug Fridge Temp (Rm 5198 Clean Utility) | Fridges | UI7 | Space | PDIGR-TE200BE24B2 | 1
Level-5 | Small Drug Fridge Fault (Rm 5198 Clean Utility) | 1 | [5 empty] | Change of State | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | Fridges-UI8 | Level 5 | Fridges | Small Drug Fridge Fault (Rm 5198 Clean Utility) | Fridges | UI8 | Space | Terminals | 1
Level-5 | Space Temp 1 | [15 empty] | Cat6 Ethernet Cable | RJ45 Connectors both sides | Space Temp |  | Space | EC - Vue Smart Sensor | 1
Level-5 | Zone 1 SSR Heating (Gen X-Ray 5403) |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L5-RD-01-UO2 | Level 5 | FCU-L5-RD-01 | Zone 1 SSR Heating (Gen X-Ray 5403) | FCU-L5-RD-01 | UO2 | FCU | SSR Module | 1
Level-5 | Zone 2 SSR Heating (Gen X-Ray 5404) |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L5-RD-01-UO3 | Level 5 | FCU-L5-RD-01 | Zone 2 SSR Heating (Gen X-Ray 5404) | FCU-L5-RD-01 | UO3 | FCU | SSR Module | 1
Level-5 | CHW Valve |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L5-RD-01-UO4 | Level 5 | FCU-L5-RD-01 | CHW Valve | FCU-L5-RD-01 | UO4 | FCU | CHWV Actuator | 1
Level-5 | HW Valve |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L5-RD-01-UO5 | Level 5 | FCU-L5-RD-01 | HW Valve | FCU-L5-RD-01 | UO5 | FCU | HHWV Actuator | 1
Level-5 | Spare |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L5-RD-01-UO6 | Level 5 | FCU-L5-RD-01 | Spare | FCU-L5-RD-01 | UO6 | FCU
Level-5 | AH LED 2 |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L5-RD-01-UO7 | Level 5 | FCU-L5-RD-01 | AH LED 2 | FCU-L5-RD-01 | UO7 | FCU | PDITE-SENSORX0 | 0
Level-5 | AH LED 3 |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L5-RD-01-UO8 | Level 5 | FCU-L5-RD-01 | AH LED 3 | FCU-L5-RD-01 | UO8 | FCU | PDITE-SENSORX0 | 0
| Sub Total | 3 | 1 | 4 | 7 | 0 | 1
Radiology – CT Scanning Rooms
Level-5 | FCU-L5-RD-02 | DI | DO | AI | AO | HLI | Prog | Condition | Timing | Priority | Graphic Name | Functionality | Frequency | [8 empty] | ECB600 | 1
Level-5 | Schedule | [5 empty] | 1 |  |  |  | FCU Iso | Display & Override | 10 Min or > 5% COV |  | FCU-L5-RD-02-SW01 | Level 5 | FCU-L5-RD-02 | Schedule | FCU-L5-RD-02 | SW01 | Software | Software Point | 1
Level-5 | Fan Enable |  | 1 | [8 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L5-RD-02-UO1 | Level 5 | FCU-L5-RD-02 | Fan Enable | FCU-L5-RD-02 | UO1 | MSSB | 12VDC Relay | 1
Level-5 | Fan Status | 1 | [5 empty] | Mismatch with enable | 60s | Critical |  | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L5-RD-02-UI1 | Level 5 | FCU-L5-RD-02 | Fan Status | FCU-L5-RD-02 | UI1 | MSSB | AFS - 930.80222524 | 1
Level-5 | SA Temp |  |  | 1 | [7 empty] | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L5-RD-02-UI2 | Level 5 | FCU-L5-RD-02 | SA Temp | FCU-L5-RD-02 | UI2 | SA Ductwork | PDIGR-TE200BE24B2 | 1
Level-5 | Spare |  |  | 1 |  |  |  | >or< Setpoint by 2°C | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L5-RD-02-UI3 | Level 5 | FCU-L5-RD-02 | Spare | FCU-L5-RD-02 | UI3 | Space
Level-5 | Space Temp 2 |  |  | 1 |  |  |  | >or< Setpoint by 2°C | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L5-RD-02-UI4 | Level 5 | FCU-L5-RD-02 | Space Temp 2 | FCU-L5-RD-02 | UI4 | Space | PDITE-SENSORX0 | 1
Level-5 | Dirty Filter | 1 | [5 empty] | Change of State | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L5-RD-02-UI5 | Level 5 | FCU-L5-RD-02 | Dirty Filter | FCU-L5-RD-02 | UI5 | Filter Box | AFS - 930.80222524 | 1
Level-5 | CZ Space Temp |  |  | 1 |  |  |  | >or< Setpoint by 2°C | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | AHU-L5-ED2-CZ-UI6 | Level 5 | AHU-L5-ED2-CZ | CZ Space Temp | AHU-L5-ED2-CZ | UI6 | Space | PDITE-SENSORX0 | 1
Level-5 | SZ Space Temp |  |  | 1 |  |  |  | >or< Setpoint by 2°C | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | AHU-L5-ED2-SZ-UI7 | Level 5 | AHU-L5-ED2-SZ | SZ Space Temp | AHU-L5-ED2-SZ | UI7 | Space | PDITE-SENSORX0 | 1
Level-5 | CZ Space Temp |  |  | 1 |  |  |  | >or< Setpoint by 2°C | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | AHU-L5-ED1-CZ-UI8 | Level 5 | AHU-L5-ED1-CZ | CZ Space Temp | AHU-L5-ED1-CZ | UI8 | Space | PDITE-SENSORX0 | 1
Level-5 | Small Drug Fridge Temp (Rm5157 Drug Store) |  |  | 1 | [7 empty] | Display / Red on Alarm | 10 Min or > 5% COV |  | Fridges-UI9 | Level 5 | Fridges | Small Drug Fridge Temp (Rm5157 Drug Store) | Fridges | UI9 | Space | PDIGR-TE200BE24B2 | 1
Level-5 | Small Drug Fridge Fault (Rm5157 Drug Store) | 1 | [5 empty] | Change of State | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | Fridges-UI10 | Level 5 | Fridges | Small Drug Fridge Fault (Rm5157 Drug Store) | Fridges | UI10 | Space | Terminals | 1
Level-5 | Space Temp 1 | [15 empty] | Cat6 Ethernet Cable | RJ45 Connectors both sides | Space Temp |  | Space | EC - Vue Smart Sensor | 1
Level-5 | Zone 1 SSR Heating (Scanning 5400) |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L5-RD-02-UO2 | Level 5 | FCU-L5-RD-02 | Zone 1 SSR Heating (Scanning 5400) | FCU-L5-RD-02 | UO2 | FCU | SSR Module | 1
Level-5 | Zone 2 SSR Heating (CT Control 5401) |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L5-RD-02-UO3 | Level 5 | FCU-L5-RD-02 | Zone 2 SSR Heating (CT Control 5401) | FCU-L5-RD-02 | UO3 | FCU | SSR Module | 1
Level-5 | CHW Valve |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L5-RD-02-UO4 | Level 5 | FCU-L5-RD-02 | CHW Valve | FCU-L5-RD-02 | UO4 | FCU | CHWV Actuator | 1
Level-5 | HW Valve |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L5-RD-02-UO5 | Level 5 | FCU-L5-RD-02 | HW Valve | FCU-L5-RD-02 | UO5 | FCU | HHWV Actuator | 1
Level-5 | Fan Speed |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L5-ED-02-UO6 | Level 5 | FCU-L5-ED-02 | Fan Speed | FCU-L5-ED-02 | UO6 | FCU | Terminals | 1
Level-5 | Spare |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L5-ED-02-UO7 | Level 5 | FCU-L5-ED-02 | Spare | FCU-L5-ED-02 | UO7 | FCU |  | 0
Level-5 | AH LED 2 |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L5-ED-02-UO8 | Level 5 | FCU-L5-ED-02 | AH LED 2 | FCU-L5-ED-02 | UO8 | FCU | PDITE-SENSORX0 | 0
Level-5 | AH LED CZ-ED-2 | [10 empty] | Display & Override | 10 Min or > 5% COV |  |  |  | AHU-L5-ED-2-CZ | AH LED CZ-ED-2 | AHU-L5-ED-2-CZ | UO9 | FCU | PDITE-SENSORX0 | 0
Level-5 | AH LED SZ-ED-2 | [10 empty] | Display & Override | 10 Min or > 5% COV |  |  |  | AHU-L5-ED-2-CZ | AH LED SZ-ED-2 | AHU-L5-ED-2-CZ | UO10 | FCU | PDITE-SENSORX0 | 0
Level-5 | AH LED CZ-ED-1 | [10 empty] | Display & Override | 10 Min or > 5% COV |  |  |  | AHU-L5-ED-1-CZ | AH LED CZ-ED-1 | AHU-L5-ED-1-CZ | UO11 | FCU | PDITE-SENSORX0 | 0
Level 6
Level 6 - Temporary AC
Level-6 | FCU-L6-01 | DI | DO | AI | AO | HLI | Prog | Condition | Timing | Priority | Graphic Name | Functionality | Frequency | [8 empty] | ECB203 | 1
Level-6 | Schedule | [5 empty] | 1 |  |  |  | FCU Iso | Display & Override | 10 Min or > 5% COV |  | FCU-L6-01-SW01 | Level-6 | FCU-L6-01 | Schedule | FCU-L6-01 | SW01 | Software | Software Point | 1
Level-6 | Fan Enable |  | 1 | [8 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L6-01-DO1 | Level-6 | FCU-L6-01 | Fan Enable | FCU-L6-01 | DO1 | MSSB | 24VAC Relay | 1
Level-6 | Fan Status | 1 | [5 empty] | Mismatch with enable | 60s | Critical |  | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L6-01-UI1 | Level-6 | FCU-L6-01 | Fan Status | FCU-L6-01 | UI1 | MSSB | CCS | 1
Level-6 | SA Temp |  |  | 1 | [7 empty] | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L6-01-UI2 | Level-6 | FCU-L6-01 | SA Temp | FCU-L6-01 | UI2 | SA Ductwork | PDIGR-TE200BE24B2 | 1
Level-6 | Space Temp |  |  | 1 |  |  |  | >or< Setpoint by 2°C | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L6-01-UI3 | Level-6 | FCU-L6-01 | Space Temp | FCU-L6-01 | UI3 | RA Ductwork | PDITE-SENSORX0 | 1
Level-6 | Dirty Filter | 1 | [5 empty] | Change of State | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L6-01-UI4 | Level-6 | FCU-L6-01 | Dirty Filter | FCU-L6-01 | UI4 | Filter Box | AFS - 930.80222524 | 1
Level-6 | Fire | 1 | [5 empty] | COS | 0s | Fire |  | Display / Red on Alarm | 10 Min or > 5% COV |  | L6 Fire-UI5 | Level-6 | FCU-L6-01 | Fire | L6 Fire | UI5 | MSSB | 24VAC Relay | 1
Level-6 | CHW Valve |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L6-01-UO6 | Level-6 | FCU-L6-01 | CHW Valve | FCU-L6-01 | UO6 | FCU | CHWV Actuator | 1
Level-6 | HW Valve |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L6-01-UO7 | Level-6 | FCU-L6-01 | HW Valve | FCU-L6-01 | UO7 | FCU | HHWV Actuator | 1
Level-6 | Fan Speed |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L6-01-UO8 | Level 5 | FCU-L6-01 | Fan Speed | FCU-L6-01 | UO8 | FCU | Terminals | 1
| Sub Total | 3 | 1 | 2 | 3 | 0 | 1
[8 empty] | Alarms |  |  | Graphics |  | History Data
Level 7
Comms Rooms
Level-7 | FCU-L7-01 | DI | DO | AI | AO | HLI | Prog | Condition | Timing | Priority | Graphic Name | Functionality | Frequency | [8 empty] | ECB203 | 1
Level-7 | Schedule | [5 empty] | 1 |  |  |  | FCU Iso | Display & Override | 10 Min or > 5% COV |  | FCU-L7-01-SW01 | Level-7 | FCU-L7-01 | Schedule | FCU-L7-01 | SW01 | Software | Software Point | 1
Level-7 | Fan Enable |  | 1 | [8 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L7-01-DO1 | Level-7 | FCU-L7-01 | Fan Enable | FCU-L7-01 | DO1 | MSSB | 24VAC Relay | 1
Level-7 | Fan Status | 1 | [5 empty] | Mismatch with enable | 60s | Critical |  | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L7-01-UI1 | Level-7 | FCU-L7-01 | Fan Status | FCU-L7-01 | UI1 | MSSB | CCS | 1
Level-7 | SA Temp |  |  | 1 | [7 empty] | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L7-01-UI2 | Level-7 | FCU-L7-01 | SA Temp | FCU-L7-01 | UI2 | SA Ductwork | PDIGR-TE200BE24B2 | 1
Level-7 | Space Temp |  |  | 1 |  |  |  | >or< Setpoint by 2°C | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L7-01-UI3 | Level-7 | FCU-L7-01 | Space Temp | FCU-L7-01 | UI3 | Space | PDITE-SENSORX0 | 1
Level-7 | Dirty Filter | 1 | [5 empty] | Change of State | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L7-01-UI4 | Level-7 | FCU-L7-01 | Dirty Filter | FCU-L7-01 | UI4 | Filter Box | AFS - 930.80222524 | 1
Level-7 | CHW Valve |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L7-01-UO6 | Level-7 | FCU-L7-01 | CHW Valve | FCU-L7-01 | UO6 | FCU | CHWV Actuator | 1
| Sub Total | 2 | 1 | 2 | 1 | 0 | 1
Lift Lobby and Corridor Areas
Level-7 | FCU-L7-02 | DI | DO | AI | AO | HLI | Prog | Condition | Timing | Priority | Graphic Name | Functionality | Frequency | [8 empty] | ECB203 | 1
Level-7 | Schedule | [5 empty] | 1 |  |  |  | FCU Iso | Display & Override | 10 Min or > 5% COV |  | FCU-L7-02-SW01 | Level-7 | FCU-L7-02 | Schedule | FCU-L7-02 | SW01 | Software | Software Point | 1
Level-7 | Fan Enable |  | 1 | [8 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L7-02-DO1 | Level-7 | FCU-L7-02 | Fan Enable | FCU-L7-02 | DO1 | MSSB | 24VAC Relay | 1
Level-7 | Fan Status | 1 | [5 empty] | Mismatch with enable | 60s | Critical |  | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L7-02-UI1 | Level-7 | FCU-L7-02 | Fan Status | FCU-L7-02 | UI1 | MSSB | CCS | 1
Level-7 | SA Temp |  |  | 1 | [7 empty] | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L7-02-UI2 | Level-7 | FCU-L7-02 | SA Temp | FCU-L7-02 | UI2 | SA Ductwork | PDIGR-TE200BE24B2 | 1
Level-7 | RA Temp |  |  | 1 |  |  |  | >or< Setpoint by 2°C | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L7-02-UI3 | Level-7 | FCU-L7-02 | RA Temp | FCU-L7-02 | UI3 | RA Ductwork | PDIGR-TE200BE24B2 | 1
Level-7 | Dirty Filter | 1 | [5 empty] | Change of State | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L7-02-UI4 | Level-7 | FCU-L7-02 | Dirty Filter | FCU-L7-02 | UI4 | Filter Box | AFS - 930.80222524 | 1
Level-7 | CHW Valve |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L7-02-UO6 | Level-7 | FCU-L7-02 | CHW Valve | FCU-L7-02 | UO6 | FCU | CHWV Actuator | 1
Level-7 | HW Valve |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L7-02-UO7 | Level-7 | FCU-L7-02 | HW Valve | FCU-L7-02 | UO7 | FCU | HHWV Actuator | 1
| Sub Total | 2 | 1 | 2 | 2 | 0 | 1
Lift Lobby and Corridor Areas
Level-7 | FCU-L7-03 | DI | DO | AI | AO | HLI | Prog | Condition | Timing | Priority | Graphic Name | Functionality | Frequency | [8 empty] | ECB203 | 1
Level-7 | Schedule | [5 empty] | 1 |  |  |  | FCU Iso | Display & Override | 10 Min or > 5% COV |  | FCU-L7-03-SW01 | Level-7 | FCU-L7-03 | Schedule | FCU-L7-03 | SW01 | Software | Software Point | 1
Level-7 | Fan Enable |  | 1 | [8 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L7-03-DO1 | Level-7 | FCU-L7-03 | Fan Enable | FCU-L7-03 | DO1 | MSSB | 24VAC Relay | 1
Level-7 | Fan Status | 1 | [5 empty] | Mismatch with enable | 60s | Critical |  | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L7-03-UI1 | Level-7 | FCU-L7-03 | Fan Status | FCU-L7-03 | UI1 | MSSB | CCS | 1
Level-7 | SA Temp |  |  | 1 | [7 empty] | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L7-03-UI2 | Level-7 | FCU-L7-03 | SA Temp | FCU-L7-03 | UI2 | SA Ductwork | PDIGR-TE200BE24B2 | 1
Level-7 | RA Temp |  |  | 1 |  |  |  | >or< Setpoint by 2°C | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L7-03-UI3 | Level-7 | FCU-L7-03 | RA Temp | FCU-L7-03 | UI3 | RA Ductwork | PDIGR-TE200BE24B2 | 1
Level-7 | Dirty Filter | 1 | [5 empty] | Change of State | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L7-03-UI4 | Level-7 | FCU-L7-03 | Dirty Filter | FCU-L7-03 | UI4 | Filter Box | AFS - 930.80222524 | 1
Level-7 | CHW Valve |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L7-03-UO6 | Level-7 | FCU-L7-03 | CHW Valve | FCU-L7-03 | UO6 | FCU | CHWV Actuator | 1
Level-7 | HW Valve |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L7-03-UO7 | Level-7 | FCU-L7-03 | HW Valve | FCU-L7-03 | UO7 | FCU | HHWV Actuator | 1
| Sub Total | 2 | 1 | 2 | 2 | 0 | 1
IMT/Maintenance Work Room
Level-7 | FCU-L7-04 | DI | DO | AI | AO | HLI | Prog | Condition | Timing | Priority | Graphic Name | Functionality | Frequency | [8 empty] | ECB203 | 1
Level-7 | Schedule | [5 empty] | 1 |  |  |  | FCU Iso | Display & Override | 10 Min or > 5% COV |  | FCU-L7-04-SW01 | Level-7 | FCU-L7-04 | Schedule | FCU-L7-04 | SW01 | Software | Software Point | 1
Level-7 | Fan Enable |  | 1 | [8 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L7-04-DO1 | Level-7 | FCU-L7-04 | Fan Enable | FCU-L7-04 | DO1 | MSSB | 24VAC Relay | 1
Level-7 | Fan Status | 1 | [5 empty] | Mismatch with enable | 60s | Critical |  | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L7-04-UI1 | Level-7 | FCU-L7-04 | Fan Status | FCU-L7-04 | UI1 | MSSB | CCS | 1
Level-7 | SA Temp |  |  | 1 | [7 empty] | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L7-04-UI2 | Level-7 | FCU-L7-04 | SA Temp | FCU-L7-04 | UI2 | SA Ductwork | PDIGR-TE200BE24B2 | 1
Level-7 | Spare |  |  | 1 |  |  |  | >or< Setpoint by 2°C | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L7-04-UI3 | Level-7 | FCU-L7-04 | Spare | FCU-L7-04 | UI3 | Space
Level-7 | Dirty Filter | 1 | [5 empty] | Change of State | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | FCU-L7-04-UI4 | Level-7 | FCU-L7-04 | Dirty Filter | FCU-L7-04 | UI4 | Filter Box | AFS - 930.80222524 | 1
Level-5 | Space Temp (Maintenance Rm) | [15 empty] | Cat6 Ethernet Cable | RJ45 Connectors both sides | Space Temp |  | Space | EC - Vue Smart Sensor | 1
Level-7 | CHW Valve |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L7-04-UO6 | Level-7 | FCU-L7-04 | CHW Valve | FCU-L7-04 | UO6 | FCU | CHWV Actuator | 1
Level-7 | HW Valve |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | FCU-L7-04-UO7 | Level-7 | FCU-L7-04 | HW Valve | FCU-L7-04 | UO7 | FCU | HHWV Actuator | 1
|  | 2 | 1 | 2 | 2 | 0 | 1
Level-7 West | MISC-L7-1 | DI | DO | AI | AO | HLI | Prog | Condition | Timing | Priority | Graphic Name | Functionality | Frequency |  |  |  |  | L7 WEST BMS Panel |  |  |  | ECB600 | 1
Fans | EF-L5-02/03 Fan Status | 1 | [5 empty] | Mismatch with enable | 60s | Critical |  | Display / Red on Alarm | 10 Min or > 5% COV |  | MISC-L7-1-UI1 | Level-7 | Iso Room | EF-L5-02/03 Fan Status | MISC-L7-1 | UI1 | EA Duct ISO 1 | AFS - 930.80222524 | 1
Fans | EF-L5-04/05 Fan Status | 1 | [5 empty] | Mismatch with enable | 60s | Critical |  | Display / Red on Alarm | 10 Min or > 5% COV |  | MISC-L7-1-UI2 | Level-7 | Iso Room | EF-L5-04/05 Fan Status | MISC-L7-1 | UI2 | EA Duct ISO 2 | AFS - 930.80222524 | 1
CRAC | CRAC-L7-1 Space Temp |  |  | 1 |  |  |  | >or< Setpoint by 2°C | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | MISC-L7-1-UI3 | Level-7 | Server Room | CRAC-L7-1 Space Temp | MISC-L7-1 | UI3 | Space | QFM2160 Temp | 1
CRAC | CRAC-L7-1 Space RH |  |  | 1 | [10 empty] | MISC-L7-1-UI4 | Level-7 | Server Room | CRAC-L7-1 Space RH | MISC-L7-1 | UI4 | Space | QFM2160 Humidity | 1
CRAC | CRAC-L7-2 Space Temp |  |  | 1 |  |  |  | >or< Setpoint by 2°C | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | MISC-L7-1-UI5 | Level-7 | Server Room | CRAC-L7-2 Space Temp | MISC-L7-1 | UI5 | Space | QFM2160 Temp | 1
CRAC | CRAC-L7-2 Space RH |  |  | 1 | [10 empty] | MISC-L7-1-UI6 | Level-7 | Server Room | CRAC-L7-2 Space RH | MISC-L7-1 | UI6 | Space | QFM2160 Humidity
CRAC | CRAC-L7-1 Wet Switch | 1 | [9 empty] | Display / Red on Alarm | 10 Min or > 5% COV |  | MISC-L7-1-UI7 | Level-7 | Server Room | CRAC-L7-1 Wet Switch | MISC-L7-1 | UI7 | Safety Tray | PT-015 (WS) | 1
CRAC | CRAC-L7-2 Wet Switch | 1 | [9 empty] | Display / Red on Alarm | 10 Min or > 5% COV |  | MISC-L7-1-UI8 | Level-7 | Server Room | CRAC-L7-2 Wet Switch | MISC-L7-1 | UI8 | Safety Tray | PT-015 (WS) | 1
VESDA | VESDA GAS Alarm #1 | 1 | [5 empty] | >or< Setpoint by 10l/s | 15min(1Hour Inhibit) | Critical |  | Display / Red on Alarm | 10 Min or > 5% COV |  | MISC-L7-1-UI9 | Level-7 | Server Room | VESDA GAS Alarm #1 | MISC-L7-1 | UI9 | Alarm Panel | Terminals | 1
VESDA | VESDA GAS Alarm #2 | 1 | [5 empty] | >or< Setpoint by 10l/s | 15min(1Hour Inhibit) | Critical |  | Display / Red on Alarm | 10 Min or > 5% COV |  | MISC-L7-1-UI10 | Level-7 | Server Room | VESDA GAS Alarm #2 | MISC-L7-1 | UI10 | Alarm Panel | Terminals | 1
VESDA | VESDA GAS Alarm #3 | 1 | [12 empty] | MISC-L7-1-UI11 | Level-7 | Server Room | VESDA GAS Alarm #3 | MISC-L7-1 | UI11 | Alarm Panel | Terminals | 1
VESDA | VESDA GAS Alarm #4 | 1 | [12 empty] | MISC-L7-1-UI12 | Level-7 | Server Room | VESDA GAS Alarm #4 | MISC-L7-1 | UI12 | Alarm Panel | Terminals | 1
Nurse Call System | Nurse Call System General Alarm | 1 | [5 empty] | COS | 0s | Fire |  | Display / Red on Alarm | 10 Min or > 5% COV |  | MISC-L7-2-UI13 | Nurse Call System | Nurse Call Panel | Nurse Call System General Alarm | MISC-L7-2 | UI13 | Nurse Call Panel | Terminals | 1
Nurse Call System | Nurse Call System Fault | 1 | [5 empty] | COS | 0s | Fire |  | Display / Red on Alarm | 10 Min or > 5% COV |  | MISC-L7-2-UI14 | Nurse Call System | Nurse Call Panel | Nurse Call System Fault | MISC-L7-2 | UI14 | Nurse Call Panel | Terminals | 1
Fire | Fire | 1 | [5 empty] | COS | 0s | Fire |  | Display / Red on Alarm | 10 Min or > 5% COV |  | MISC-L7-1-UI15 | Level-7 | Fire | Fire | MISC-L7-1 | UI15 | MSSB | Terminals | 1
ISO-1 | EF-L5-02/03 EA Damper |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | MISC-L7-1-UO1 | Level-7 | Iso Room | EF-L5-02/03 EA Damper | MISC-L7-1 | UO1 | EA Duct ISO 1 | GDB161.1E | 1
ISO-1 | EF-L5-04/05 EA Damper |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | MISC-L7-1-UO2 | Level-7 | Iso Room | EF-L5-04/05 EA Damper | MISC-L7-1 | UO2 | EA Duct ISO 1 | GDB161.1E | 1
Fans | OAF-L7-01 Fan Enable |  | 1 | [8 empty] | Display & Override | 10 Min or > 5% COV |  | MISC-L7-1-UO3 | Level-7 | Fans | OAF-L7-01 Fan Enable | MISC-L7-1 | UO3 | MSSB | 12VDC Relay | 1
Fans | OAF-L7-02 Fan Enable |  | 1 | [8 empty] | Display & Override | 10 Min or > 5% COV |  | MISC-L7-1-UO4 | Level-7 | Fans | OAF-L7-02 Fan Enable | MISC-L7-1 | UO4 | MSSB | 12VDC Relay | 1
Fans | OAF-L7-03 Fan Enable |  | 1 | [8 empty] | Display & Override | 10 Min or > 5% COV |  | MISC-L7-1-UO5 | Level-7 | Fans | OAF-L7-03 Fan Enable | MISC-L7-1 | UO5 | MSSB | 12VDC Relay | 1
| Sub Total | 9 | 3 | 4 | 2 | 0 | 0
Level 7 East | MISC-L7-2 | DI | DO | AI | AO | HLI | Prog | Condition | Timing | Priority | Graphic Name | Functionality | Frequency |  |  |  |  | L7 EAST BMS Panel |  |  |  | ECB600 | 1 | (i)
Med Gas | Gas Alarm Panel Fault | 1 | [12 empty] | MISC-L7-2-UI1 | Med Gas | Med Gas | Gas Alarm Panel Fault | MISC-L7-2 | UI1 | Med Gas | Terminals | 1
Vacuum Pump | Vacuum Pump 1 Status | 1 | [12 empty] | MISC-L7-2-UI2 | Vacuum Pump | Vacuum Pump | Vacuum Pump 1 Status | MISC-L7-2 | UI2 | Vacuum Pump | Terminals | 1
Vacuum Pump | Vacuum Pump 2 Status | 1 | [12 empty] | MISC-L7-2-UI3 | Vacuum Pump | Vacuum Pump | Vacuum Pump 2 Status | MISC-L7-2 | UI3 | Vacuum Pump | Terminals | 1
Compressed Air | Compressor Status | 1 | [12 empty] | MISC-L7-2-UI4 | Compressed Air | Compressed Air | Compressor Status | MISC-L7-2 | UI4 | Compressed Air | Terminals | 1
Fire | Fire Alarm | 1 | [12 empty] | MISC-L7-2-UI5 | Fire | Fire | Fire Alarm | MISC-L7-2 | UI5 | Fire | Terminals | 1
Fire | Fire Panel Fault x | 1 | [12 empty] | MISC-L7-2-UI6 | Fire | Fire | Fire Panel Fault x | MISC-L7-2 | UI6 | Fire | Terminals | 1
Fire | EWIS Alarm | 1 | [12 empty] | MISC-L7-2-UI7 | Fire | Fire | EWIS Alarm | MISC-L7-2 | UI7 | Fire | Terminals | 1
Fire | EWIS Fault | 1 | [12 empty] | MISC-L7-2-UI8 | Fire | Fire | EWIS Fault | MISC-L7-2 | UI8 | Fire | Terminals | 1
Lifts | Lifts Status | 1 | [8 empty] | LIFT | Display only | COV |  | MISC-L7-2-UI9 | Lifts | Lifts | Lifts Status | MISC-L7-2 | UI9 | Lifts | Lift Terminals | 1
Lifts | Lifts Fault | 1 | [5 empty] | Change Of State | 60s | Critical |  | Display / Red on Alarm | COV |  | MISC-L7-2-UI10 | Lifts | Lifts | Lifts Fault | MISC-L7-2 | UI10 | Lifts | Lift Terminals | 1
Fans | OAF-L7-01 Status | 1 | [12 empty] | MISC-L7-1-UI11 | Level-7 | Fans | OAF-L7-01 Status | MISC-L7-1 | UI11 | MSSB | CCS | 1
Fans | OAF-L7-02 Status | 1 | [12 empty] | MISC-L7-1-UI12 | Level-7 | Fans | OAF-L7-02 Status | MISC-L7-1 | UI12 | MSSB | CCS | 1
Fans | OAF-L7-03 Status | 1 | [12 empty] | MISC-L7-1-UI13 | Level-7 | Fans | OAF-L7-03 Status | MISC-L7-1 | UI13 | MSSB | CCS | 1
Vacuum Pump | Vacuum Pump 1 Start/Stop |  | 1 | [11 empty] | MISC-L7-2-UO1 | Vacuum Pump | Vacuum Pump | Vacuum Pump 1 Start/Stop | MISC-L7-2 | UO1 | Vacuum Pump | 12VDC Relay | 1
Vacuum Pump | Vacuum Pump 2 Start/Stop |  | 1 | [11 empty] | MISC-L7-2-UO2 | Vacuum Pump | Vacuum Pump | Vacuum Pump 2 Start/Stop | MISC-L7-2 | UO2 | Vacuum Pump | 12VDC Relay | 1
Compressed Air | Compressor Start / Stop |  | 1 | [11 empty] | MISC-L7-2-UO3 | Compressed Air | Compressed Air | Compressor Start / Stop | MISC-L7-2 | UO3 | Compressed Air | 12VDC Relay | 1
Fans | OAF-L7-01 Fan Enable |  | 1 | [8 empty] | Display & Override | 10 Min or > 5% COV |  | MISC-L7-1-UO4 | Level-7 | Fans | OAF-L7-01 Fan Enable | MISC-L7-1 | UO4 | MSSB | 12VDC Relay | 1
Fans | OAF-L7-02 Fan Enable |  | 1 | [8 empty] | Display & Override | 10 Min or > 5% COV |  | MISC-L7-1-UO5 | Level-7 | Fans | OAF-L7-02 Fan Enable | MISC-L7-1 | UO5 | MSSB | 12VDC Relay | 1
Fans | OAF-L7-03 Fan Enable |  | 1 | [8 empty] | Display & Override | 10 Min or > 5% COV |  | MISC-L7-1-UO6 | Level-7 | Fans | OAF-L7-03 Fan Enable | MISC-L7-1 | UO6 | MSSB | 12VDC Relay | 1
| Sub Total | 13 | 3 | 0 | 0 | 0 | 0
Level 5 Emergency Department Support
Level-7 | AHU-L5-ED1 | DI | DO | AI | AO | HLI | Prog | Condition | Timing | Priority | Graphic Name | Functionality | Frequency | [8 empty] | ECB600 | 1
Level-7 | Schedule | [5 empty] | 1 |  |  |  | AHU ED | Display & Override | 10 Min or > 5% COV |  | AHU-L5-ED1-SW01 | Level-7 | AHU-L5-ED1 | Schedule | AHU-L5-ED1 | SW01 | Software | Software Point | 1
Level-7 | CHW Offcoil Temp |  |  | 1 |  |  |  | >or< Setpoint by 2°C | 15min(1Hour Inhibit) |  |  | Display & Override | 10 Min or > 5% COV |  | AHU-L5-ED1-UI1 | Level-7 | AHU-L5-ED1 | CHW Offcoil Temp | AHU-L5-ED1 | UI1 | Plenum Offcoil | PDIGR-TE200FDB24A | 1
Level-7 | RA Temp |  |  | 1 |  |  |  | >or< Setpoint by 2°C | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | AHU-L5-ED1-UI2 | Level-7 | AHU-L5-ED1 | RA Temp | AHU-L5-ED1 | UI2 | RA Ductwork | QFM2160 Temp | 1
Level-7 | RA Humidity |  |  | 1 |  |  |  | >or< Setpoint by 5% | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | AHU-L5-ED1-UI3 | Level-7 | AHU-L5-ED1 | RA Humidity | AHU-L5-ED1 | UI3 | RA Ductwork | QFM2160 Humidity | 1
Level-7 | Dirty Filter | 1 | [5 empty] | Change of State | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | AHU-L5-ED1-UI4 | Level-7 | AHU-L5-ED1 | Dirty Filter | AHU-L5-ED1 | UI4 | Filter Box | AFS - 930.80222524 | 1
Level-7 | NZ SA Temp |  |  | 1 |  |  |  | >or< Setpoint by 2°C | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | AHU-L5-ED1-UI5 | Level-7 | AHU-L5-ED1 | NZ SA Temp | AHU-L5-ED1 | UI5 | Zone SA Ductwork | PDIGR-TE200BE24B2 | 1
Level-7 | SZ SA Temp |  |  | 1 |  |  |  | >or< Setpoint by 2°C | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | AHU-L5-ED1-UI6 | Level-7 | AHU-L5-ED1 | SZ SA Temp | AHU-L5-ED1 | UI6 | Zone SA Ductwork | PDIGR-TE200BE24B2 | 1
Level-7 | WZ SA Temp |  |  | 1 |  |  |  | >or< Setpoint by 2°C | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | AHU-L5-ED1-UI7 | Level-7 | AHU-L5-ED1 | WZ SA Temp | AHU-L5-ED1 | UI7 | Zone SA Ductwork | PDIGR-TE200BE24B2 | 1
Level-7 | CZ SA Temp |  |  | 1 |  |  |  | >or< Setpoint by 2°C | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | AHU-L5-ED1-UI8 | Level-7 | AHU-L5-ED1 | CZ SA Temp | AHU-L5-ED1 | UI8 | Zone SA Ductwork | PDIGR-TE200BE24B2 | 1
Level-7 | CHW Valve |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | AHU-L5-ED1-UO1 | Level-7 | AHU-L5-ED1 | CHW Valve | AHU-L5-ED1 | UO1 | AHU | CHWV Actuator | 1
Level-7 | OA Damper |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | AHU-L5-ED1-UO2 | Level-7 | AHU-L5-ED1 | OA Damper | AHU-L5-ED1 | UO2 | AHU | GDB161.1E | 1
Level-7 | EA Damper |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | AHU-L5-ED1-UO3 | Level-7 | AHU-L5-ED1 | EA Damper | AHU-L5-ED1 | UO3 | AHU | GDB161.1E | 1
Level-7 | RA Damper |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | AHU-L5-ED1-UO4 | Level-7 | AHU-L5-ED1 | RA Damper | AHU-L5-ED1 | UO4 | AHU | GDB161.1E | 1
Level-7 | NZ F&B Actuator |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | AHU-L5-ED1-UO5 | Level-7 | AHU-L5-ED1 | NZ F&B Actuator | AHU-L5-ED1 | UO5 | AHU | GDB161.1E | 2
Level-7 | SZ F&B Actuator |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | AHU-L5-ED1-UO6 | Level-7 | AHU-L5-ED1 | SZ F&B Actuator | AHU-L5-ED1 | UO6 | AHU | GDB161.1E | 2
Level-7 | WZ F&B Actuator |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | AHU-L5-ED1-UO7 | Level-7 | AHU-L5-ED1 | WZ F&B Actuator | AHU-L5-ED1 | UO7 | AHU | GDB161.1E | 2
Level-7 | CZ F&B Actuator |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | AHU-L5-ED1-UO8 | Level-7 | AHU-L5-ED1 | CZ F&B Actuator | AHU-L5-ED1 | UO8 | AHU | GDB161.1E | 2
Level-7 | NZ HW Valve |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | AHU-L5-ED1-UO9 | Level-7 | AHU-L5-ED1 | NZ HW Valve | AHU-L5-ED1 | UO9 | AHU | HHWV Actuator | 1
Level-7 | SZ HW Valve |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | AHU-L5-ED1-UO10 | Level-7 | AHU-L5-ED1 | SZ HW Valve | AHU-L5-ED1 | UO10 | AHU | HHWV Actuator | 1
Level-7 | WZ HW Valve |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | AHU-L5-ED1-UO11 | Level-7 | AHU-L5-ED1 | WZ HW Valve | AHU-L5-ED1 | UO11 | AHU | HHWV Actuator | 1
Level-7 | CZ HW Valve |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | AHU-L5-ED1-UO12 | Level-7 | AHU-L5-ED1 | CZ HW Valve | AHU-L5-ED1 | UO12 | AHU | HHWV Actuator | 1
| Sub Total | 1 | 0 | 7 | 12 | 0 | 1
Level 5 Emergency Department
Level-7 | AHU-L5-ED2 | DI | DO | AI | AO | HLI | Prog | Condition | Timing | Priority | Graphic Name | Functionality | Frequency | [8 empty] | ECB600 | 1
Level-7 | Schedule | [5 empty] | 1 |  |  |  | AHU ED | Display & Override | 10 Min or > 5% COV |  | AHU-L5-ED2-SW01 | Level-7 | AHU-L5-ED2 | Schedule | AHU-L5-ED2 | SW01 | Software | Software Point | 1
Level-7 | CHW Offcoil Temp |  |  | 1 |  |  |  | >or< Setpoint by 2°C | 15min(1Hour Inhibit) |  |  | Display & Override | 10 Min or > 5% COV |  | AHU-L5-ED2-UI1 | Level-7 | AHU-L5-ED2 | CHW Offcoil Temp | AHU-L5-ED2 | UI1 | Plenum Offcoil | PDIGR-TE200FDB24A | 1
Level-7 | RA Temp |  |  | 1 |  |  |  | >or< Setpoint by 2°C | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | AHU-L5-ED2-UI2 | Level-7 | AHU-L5-ED2 | RA Temp | AHU-L5-ED2 | UI2 | RA Ductwork | QFM2160 Temp | 1
Level-7 | RA Humidity |  |  | 1 |  |  |  | >or< Setpoint by 5% | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | AHU-L5-ED2-UI3 | Level-7 | AHU-L5-ED2 | RA Humidity | AHU-L5-ED2 | UI3 | RA Ductwork | QFM2160 Humidity | 1
Level-7 | Dirty Filter | 1 | [5 empty] | Change of State | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | AHU-L5-ED2-UI4 | Level-7 | AHU-L5-ED2 | Dirty Filter | AHU-L5-ED2 | UI4 | Filter Box | AFS - 930.80222524 | 1
Level-7 | NZ SA Temp |  |  | 1 |  |  |  | >or< Setpoint by 2°C | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | AHU-L5-ED2-UI5 | Level-7 | AHU-L5-ED2 | NZ SA Temp | AHU-L5-ED2 | UI5 | Zone SA Ductwork | PDIGR-TE200BE24B2 | 1
Level-7 | SZ SA Temp |  |  | 1 |  |  |  | >or< Setpoint by 2°C | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | AHU-L5-ED2-UI6 | Level-7 | AHU-L5-ED2 | SZ SA Temp | AHU-L5-ED2 | UI6 | Zone SA Ductwork | PDIGR-TE200BE24B2 | 1
Level-7 | EZ SA Temp |  |  | 1 |  |  |  | >or< Setpoint by 2°C | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | AHU-L5-ED2-UI7 | Level-7 | AHU-L5-ED2 | EZ SA Temp | AHU-L5-ED2 | UI7 | Zone SA Ductwork | PDIGR-TE200BE24B2 | 1
Level-7 | CZ SA Temp |  |  | 1 |  |  |  | >or< Setpoint by 2°C | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | AHU-L5-ED2-UI8 | Level-7 | AHU-L5-ED2 | CZ SA Temp | AHU-L5-ED2 | UI8 | Zone SA Ductwork | PDIGR-TE200BE24B2 | 1
Level-7 | CHW Valve |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | AHU-L5-ED2-UO1 | Level-7 | AHU-L5-ED2 | CHW Valve | AHU-L5-ED2 | UO1 | AHU | CHWV Actuator | 1
Level-7 | OA Damper |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | AHU-L5-ED2-UO2 | Level-7 | AHU-L5-ED2 | OA Damper | AHU-L5-ED2 | UO2 | AHU | GDB161.1E | 1
Level-7 | EA Damper |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | AHU-L5-ED2-UO3 | Level-7 | AHU-L5-ED2 | EA Damper | AHU-L5-ED2 | UO3 | AHU | GDB161.1E | 1
Level-7 | RA Damper |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | AHU-L5-ED2-UO4 | Level-7 | AHU-L5-ED2 | RA Damper | AHU-L5-ED2 | UO4 | AHU | GDB161.1E | 1
Level-7 | NZ F&B Actuator |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | AHU-L5-ED2-UO5 | Level-7 | AHU-L5-ED2 | NZ F&B Actuator | AHU-L5-ED2 | UO5 | AHU | GDB161.1E | 2
Level-7 | SZ F&B Actuator |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | AHU-L5-ED2-UO6 | Level-7 | AHU-L5-ED2 | SZ F&B Actuator | AHU-L5-ED2 | UO6 | AHU | GDB161.1E | 2
Level-7 | EZ F&B Actuator |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | AHU-L5-ED2-UO7 | Level-7 | AHU-L5-ED2 | EZ F&B Actuator | AHU-L5-ED2 | UO7 | AHU | GDB161.1E | 2
Level-7 | CZ F&B Actuator |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | AHU-L5-ED2-UO8 | Level-7 | AHU-L5-ED2 | CZ F&B Actuator | AHU-L5-ED2 | UO8 | AHU | GDB161.1E | 2
Level-7 | NZ HW Valve |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | AHU-L5-ED2-UO9 | Level-7 | AHU-L5-ED2 | NZ HW Valve | AHU-L5-ED2 | UO9 | AHU | HHWV Actuator | 1
Level-7 | SZ HW Valve |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | AHU-L5-ED2-UO10 | Level-7 | AHU-L5-ED2 | SZ HW Valve | AHU-L5-ED2 | UO10 | AHU | HHWV Actuator | 1
Level-7 | EZ HW Valve |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | AHU-L5-ED2-UO11 | Level-7 | AHU-L5-ED2 | EZ HW Valve | AHU-L5-ED2 | UO11 | AHU | HHWV Actuator | 1
Level-7 | CZ HW Valve |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | AHU-L5-ED2-UO12 | Level-7 | AHU-L5-ED2 | CZ HW Valve | AHU-L5-ED2 | UO12 | AHU | HHWV Actuator | 1
| SAF-L5-ED1 | DI | DO | AI | AO | HLI | Prog | Condition | Timing | Priority | Graphic Name | Functionality | Frequency | [8 empty] | VSD-SAF-L5-ED1
Vent Fans | Enable |  |  |  |  | 1 |  |  |  |  | SAF-L5-ED1 | Display & Override | COV |  | SAF-L5-ED1-SW01 | Level-7 | SAF-L5-ED1 | Enable | SAF-L5-ED1 | SW01 | Level-7 | -
Vent Fans | Status |  |  |  |  | 1 |  | Mismatch with enable | 60s | Critical |  | Display / Red on Alarm | COV |  | SAF-L5-ED1-SW02 | Level-7 | SAF-L5-ED1 | Status | SAF-L5-ED1 | SW02 | Level-7 | -
Vent Fans | VSD Fault |  |  |  |  | 1 |  | Change Of State | 60s | Critical |  | Display / Red on Alarm | COV |  | SAF-L5-ED1-SW03 | Level-7 | SAF-L5-ED1 | VSD Fault | SAF-L5-ED1 | SW03 | Level-7 | -
Vent Fans | VSD Speed Control |  |  |  |  | 1 | [5 empty] | Display Only | 60s |  | SAF-L5-ED1-SW04 | Level-7 | SAF-L5-ED1 | VSD Speed Control | SAF-L5-ED1 | SW04 | Level-7 | -
| RAF-L5-ED1 | DI | DO | AI | AO | HLI | Prog | Condition | Timing | Priority | Graphic Name | Functionality | Frequency | [8 empty] | VSD-RAF-L5-ED1
Vent Fans | Enable |  |  |  |  | 1 |  |  |  |  | RAF-L5-ED1 | Display & Override | COV |  | RAF-L5-ED1-SW01 | Level-7 | RAF-L5-ED1 | Enable | RAF-L5-ED1 | SW01 | Level-7 | -
Vent Fans | Status |  |  |  |  | 1 |  | Mismatch with enable | 60s | Critical |  | Display / Red on Alarm | COV |  | RAF-L5-ED1-SW02 | Level-7 | RAF-L5-ED1 | Status | RAF-L5-ED1 | SW02 | Level-7 | -
Vent Fans | VSD Fault |  |  |  |  | 1 |  | Change Of State | 60s | Critical |  | Display / Red on Alarm | COV |  | RAF-L5-ED1-SW03 | Level-7 | RAF-L5-ED1 | VSD Fault | RAF-L5-ED1 | SW03 | Level-7 | -
Vent Fans | VSD Speed Control |  |  |  |  | 1 | [5 empty] | Display Only | 60s |  | RAF-L5-ED1-SW04 | Level-7 | RAF-L5-ED1 | VSD Speed Control | RAF-L5-ED1 | SW04 | Level-7 | -
| Sub Total | 0 | 0 | 0 | 0 | 4 | 0
| SAF-L5-ED2 | DI | DO | AI | AO | HLI | Prog | Condition | Timing | Priority | Graphic Name | Functionality | Frequency | [8 empty] | VSD-SAF-L5-ED2
Vent Fans | Enable |  |  |  |  | 1 |  |  |  |  | SAF-L5-ED2 | Display & Override | COV |  | SAF-L5-ED2-SW01 | Level-7 | SAF-L5-ED2 | Enable | SAF-L5-ED2 | SW01 | Level-7 | -
Vent Fans | Status |  |  |  |  | 1 |  | Mismatch with enable | 60s | Critical |  | Display / Red on Alarm | COV |  | SAF-L5-ED2-SW02 | Level-7 | SAF-L5-ED2 | Status | SAF-L5-ED2 | SW02 | Level-7 | -
Vent Fans | VSD Fault |  |  |  |  | 1 |  | Change Of State | 60s | Critical |  | Display / Red on Alarm | COV |  | SAF-L5-ED2-SW03 | Level-7 | SAF-L5-ED2 | VSD Fault | SAF-L5-ED2 | SW03 | Level-7 | -
Vent Fans | VSD Speed Control |  |  |  |  | 1 | [5 empty] | Display Only | 60s |  | SAF-L5-ED2-SW04 | Level-7 | SAF-L5-ED2 | VSD Speed Control | SAF-L5-ED2 | SW04 | Level-7 | -
| Sub Total | 0 | 0 | 0 | 0 | 4 | 0
| RAF-L5-ED2 | DI | DO | AI | AO | HLI | Prog | Condition | Timing | Priority | Graphic Name | Functionality | Frequency | [8 empty] | VSD-RAF-L5-ED2
Vent Fans | Enable |  |  |  |  | 1 |  |  |  |  | RAF-L5-ED2 | Display & Override | COV |  | RAF-L5-ED2-SW01 | Level-7 | RAF-L5-ED2 | Enable | RAF-L5-ED2 | SW01 | Level-7 | -
Vent Fans | Status |  |  |  |  | 1 |  | Mismatch with enable | 60s | Critical |  | Display / Red on Alarm | COV |  | RAF-L5-ED2-SW02 | Level-7 | RAF-L5-ED2 | Status | RAF-L5-ED2 | SW02 | Level-7 | -
Vent Fans | VSD Fault |  |  |  |  | 1 |  | Change Of State | 60s | Critical |  | Display / Red on Alarm | COV |  | RAF-L5-ED2-SW03 | Level-7 | RAF-L5-ED2 | VSD Fault | RAF-L5-ED2 | SW03 | Level-7 | -
Vent Fans | VSD Speed Control |  |  |  |  | 1 | [5 empty] | Display Only | 60s |  | RAF-L5-ED2-SW04 | Level-7 | RAF-L5-ED2 | VSD Speed Control | RAF-L5-ED2 | SW04 | Level-7 | -
| Sub Total | 0 | 0 | 0 | 0 | 4 | 0
Level 4 Renal Department
Level-7 | AHU-L4-RN | DI | DO | AI | AO | HLI | Prog | Condition | Timing | Priority | Graphic Name | Functionality | Frequency | [8 empty] | ECB600 | 1
Level-7 | Schedule | [5 empty] | 1 |  |  |  | AHU ED | Display & Override | 10 Min or > 5% COV |  | AHU-L4-RN-SW01 | Level-7 | AHU-L4-RN | Schedule | AHU-L4-RN | SW01 | Software | Software Point | 1
Level-7 | CHW Offcoil Temp |  | 1 |  |  |  |  | >or< Setpoint by 2°C | 15min(1Hour Inhibit) |  |  | Display & Override | 10 Min or > 5% COV |  | AHU-L4-RN-UI1 | Level-7 | AHU-L4-RN | CHW Offcoil Temp | AHU-L4-RN | UI1 | Plenum Offcoil | PDIGR-TE200FDB24A | 1
Level-7 | RA Temp |  |  | 1 |  |  |  | >or< Setpoint by 2°C | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | AHU-L4-RN-UI2 | Level-7 | AHU-L4-RN | RA Temp | AHU-L4-RN | UI2 | RA Ductwork | QFM2160 Temp | 1
Level-7 | RA Humidity |  |  | 1 |  |  |  | >or< Setpoint by 5% | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | AHU-L4-RN-UI3 | Level-7 | AHU-L4-RN | RA Humidity | AHU-L4-RN | UI3 | RA Ductwork | QFM2160 Humidity | 1
Level-7 | Dirty Filter | 1 | [5 empty] | Change of State | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | AHU-L4-RN-UI4 | Level-7 | AHU-L4-RN | Dirty Filter | AHU-L4-RN | UI4 | Filter Box | AFS - 930.80222524 | 1
Level-7 | NZ SA Temp |  |  | 1 |  |  |  | >or< Setpoint by 2°C | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | AHU-L4-RN-UI5 | Level-7 | AHU-L4-RN | NZ SA Temp | AHU-L4-RN | UI5 | Zone SA Ductwork | PDIGR-TE200BE24B2 | 1
Level-7 | SZ SA Temp |  |  | 1 |  |  |  | >or< Setpoint by 2°C | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | AHU-L4-RN-UI6 | Level-7 | AHU-L4-RN | SZ SA Temp | AHU-L4-RN | UI6 | Zone SA Ductwork | PDIGR-TE200BE24B2 | 1
Level-7 | WZ SA Temp |  |  | 1 |  |  |  | >or< Setpoint by 2°C | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | AHU-L4-RN-UI7 | Level-7 | AHU-L4-RN | WZ SA Temp | AHU-L4-RN | UI7 | Zone SA Ductwork | PDIGR-TE200BE24B2 | 1
Level-7 | CZ SA Temp |  |  | 1 |  |  |  | >or< Setpoint by 2°C | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | AHU-L4-RN-UI8 | Level-7 | AHU-L4-RN | CZ SA Temp | AHU-L4-RN | UI8 | Zone SA Ductwork | PDIGR-TE200BE24B2 | 1
Level-7 | CHW Valve |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | AHU-L4-RN-UO1 | Level-7 | AHU-L4-RN | CHW Valve | AHU-L4-RN | UO1 | AHU | CHWV Actuator | 1
Level-7 | OA Damper |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | AHU-L4-RN-UO2 | Level-7 | AHU-L4-RN | OA Damper | AHU-L4-RN | UO2 | AHU | GDB161.1E | 1
Level-7 | EA Damper |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | AHU-L4-RN-UO3 | Level-7 | AHU-L4-RN | EA Damper | AHU-L4-RN | UO3 | AHU | GDB161.1E | 1
Level-7 | RA Damper |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | AHU-L4-RN-UO4 | Level-7 | AHU-L4-RN | RA Damper | AHU-L4-RN | UO4 | AHU | GDB161.1E | 1
Level-7 | NZ F&B Actuator |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | AHU-L4-RN-UO5 | Level-7 | AHU-L4-RN | NZ F&B Actuator | AHU-L4-RN | UO5 | AHU | GDB161.1E | 2
Level-7 | SZ F&B Actuator |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | AHU-L4-RN-UO6 | Level-7 | AHU-L4-RN | SZ F&B Actuator | AHU-L4-RN | UO6 | AHU | GDB161.1E | 2
Level-7 | WZ F&B Actuator |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | AHU-L4-RN-UO7 | Level-7 | AHU-L4-RN | WZ F&B Actuator | AHU-L4-RN | UO7 | AHU | GDB161.1E | 2
Level-7 | CZ F&B Actuator |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | AHU-L4-RN-UO8 | Level-7 | AHU-L4-RN | CZ F&B Actuator | AHU-L4-RN | UO8 | AHU | GDB161.1E | 2
Level-7 | NZ HW Valve |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | AHU-L4-RN-UO9 | Level-7 | AHU-L4-RN | NZ HW Valve | AHU-L4-RN | UO9 | AHU | HHWV Actuator | 1
Level-7 | SZ HW Valve |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | AHU-L4-RN-UO10 | Level-7 | AHU-L4-RN | SZ HW Valve | AHU-L4-RN | UO10 | AHU | HHWV Actuator | 1
Level-7 | WZ HW Valve |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | AHU-L4-RN-UO11 | Level-7 | AHU-L4-RN | WZ HW Valve | AHU-L4-RN | UO11 | AHU | HHWV Actuator | 1
Level-7 | CZ HW Valve |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | AHU-L4-RN-UO12 | Level-7 | AHU-L4-RN | CZ HW Valve | AHU-L4-RN | UO12 | AHU | HHWV Actuator | 1
| Sub Total | 1 | 1 | 6 | 12 | 0 | 1
Level 4 Emergency Department
Level-7 | AHU-L4-EDS | DI | DO | AI | AO | HLI | Prog | Condition | Timing | Priority | Graphic Name | Functionality | Frequency | [8 empty] | ECB600 | 1
Level-7 | CHW Offcoil Temp |  |  | 1 |  |  |  | >or< Setpoint by 2°C | 15min(1Hour Inhibit) |  |  | Display & Override | 10 Min or > 5% COV |  | AHU-L4-EDS-UI1 | Level-7 | AHU-L4-EDS | CHW Offcoil Temp | AHU-L4-EDS | UI1 | Plenum Offcoil | PDIGR-TE200FDB24A | 1
Level-7 | RA Temp |  |  | 1 |  |  |  | >or< Setpoint by 2°C | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | AHU-L4-EDS-UI2 | Level-7 | AHU-L4-EDS | RA Temp | AHU-L4-EDS | UI2 | RA Ductwork | QFM2160 Temp | 1
Level-7 | RA Humidity |  |  | 1 |  |  |  | >or< Setpoint by 5% | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | AHU-L4-EDS-UI3 | Level-7 | AHU-L4-EDS | RA Humidity | AHU-L4-EDS | UI3 | RA Ductwork | QFM2160 Humidity | 1
Level-7 | Dirty Filter | 1 | [5 empty] | Change of State | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | AHU-L4-EDS-UI4 | Level-7 | AHU-L4-EDS | Dirty Filter | AHU-L4-EDS | UI4 | Filter Box | AFS - 930.80222524 | 1
Level-7 | NZ SA Temp |  |  | 1 |  |  |  | >or< Setpoint by 2°C | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | AHU-L4-EDS-UI5 | Level-7 | AHU-L4-EDS | NZ SA Temp | AHU-L4-EDS | UI5 | Zone SA Ductwork | PDIGR-TE200BE24B2 | 1
Level-7 | CZ SA Temp |  |  | 1 |  |  |  | >or< Setpoint by 2°C | 15min(1Hour Inhibit) |  |  | Display / Red on Alarm | 10 Min or > 5% COV |  | AHU-L4-EDS-UI6 | Level-7 | AHU-L4-EDS | CZ SA Temp | AHU-L4-EDS | UI6 | Zone SA Ductwork | PDIGR-TE200BE24B2 | 1
Level-7 | Ambient Temperature |  |  | 1 | [7 empty] | Display only | COV |  | Ambient Temperature-UI7 | Level-7 | Ambient Temperature | Ambient Temperature | Ambient Temperature | UI7 | Level-7 | QFM2160 Temp | 1
Level-7 | Ambient Humidity |  |  | 1 | [7 empty] | Display only | COV |  | Ambient Humidity-UI8 | Level-7 | Ambient Humidity | Ambient Humidity | Ambient Humidity | UI8 | Level-7 | QFM2160 Humidity | 1
Level-7 | CHW Valve |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | AHU-L4-EDS-UO1 | Level-7 | AHU-L4-EDS | CHW Valve | AHU-L4-EDS | UO1 | AHU | CHWV Actuator | 1
Level-7 | OA Damper |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | AHU-L4-EDS-UO2 | Level-7 | AHU-L4-EDS | OA Damper | AHU-L4-EDS | UO2 | AHU | GDB161.1E | 1
Level-7 | EA Damper |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | AHU-L4-EDS-UO3 | Level-7 | AHU-L4-EDS | EA Damper | AHU-L4-EDS | UO3 | AHU | GDB161.1E | 1
Level-7 | RA Damper |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | AHU-L4-EDS-UO4 | Level-7 | AHU-L4-EDS | RA Damper | AHU-L4-EDS | UO4 | AHU | GDB161.1E | 1
Level-7 | NZ F&B Actuator |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | AHU-L4-EDS-UO5 | Level-7 | AHU-L4-EDS | NZ F&B Actuator | AHU-L4-EDS | UO5 | AHU | GDB161.1E | 2
Level-7 | CZ F&B Actuator |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | AHU-L4-EDS-UO6 | Level-7 | AHU-L4-EDS | CZ F&B Actuator | AHU-L4-EDS | UO6 | AHU | GDB161.1E | 2
Level-7 | NZ HW Valve |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | AHU-L4-EDS-UO9 | Level-7 | AHU-L4-EDS | NZ HW Valve | AHU-L4-EDS | UO9 | AHU | HHWV Actuator | 1
Level-7 | CZ HW Valve |  |  |  | 1 | [6 empty] | Display & Override | 10 Min or > 5% COV |  | AHU-L4-EDS-UO10 | Level-7 | AHU-L4-EDS | CZ HW Valve | AHU-L4-EDS | UO10 | AHU | HHWV Actuator | 1
| Sub Total | 1 | 0 | 7 | 8 | 0 | 0
| SAF-L4-RN | DI | DO | AI | AO | HLI | Prog | Condition | Timing | Priority | Graphic Name | Functionality | Frequency | [8 empty] | VSD-SAF-L4-RN
Vent Fans | Enable |  |  |  |  | 1 |  |  |  |  | SAF-L4-RN | Display & Override | COV |  | SAF-L4-RN-SW01 | Level-7 | SAF-L4-RN | Enable | SAF-L4-RN | SW01 | Level-7 | -
Vent Fans | Status |  |  |  |  | 1 |  | Mismatch with enable | 60s | Critical |  | Display / Red on Alarm | COV |  | SAF-L4-RN-SW02 | Level-7 | SAF-L4-RN | Status | SAF-L4-RN | SW02 | Level-7 | -
Vent Fans | VSD Fault |  |  |  |  | 1 |  | Change Of State | 60s | Critical |  | Display / Red on Alarm | COV |  | SAF-L4-RN-SW03 | Level-7 | SAF-L4-RN | VSD Fault | SAF-L4-RN | SW03 | Level-7 | -
Vent Fans | VSD Speed Control |  |  |  |  | 1 | [5 empty] | Display Only | 60s |  | SAF-L4-RN-SW04 | Level-7 | SAF-L4-RN | VSD Speed Control | SAF-L4-RN | SW04 | Level-7 | -
| RAF-L4-RN | DI | DO | AI | AO | HLI | Prog | Condition | Timing | Priority | Graphic Name | Functionality | Frequency | [8 empty] | VSD-RAF-L4-RN
Vent Fans | Enable |  |  |  |  | 1 |  |  |  |  | RAF-L4-RN | Display & Override | COV |  | RAF-L4-RN-SW01 | Level-7 | RAF-L4-RN | Enable | RAF-L4-RN | SW01 | Level-7 | -
Vent Fans | Status |  |  |  |  | 1 |  | Mismatch with enable | 60s | Critical |  | Display / Red on Alarm | COV |  | RAF-L4-RN-SW02 | Level-7 | RAF-L4-RN | Status | RAF-L4-RN | SW02 | Level-7 | -
Vent Fans | VSD Fault |  |  |  |  | 1 |  | Change Of State | 60s | Critical |  | Display / Red on Alarm | COV |  | RAF-L4-RN-SW03 | Level-7 | RAF-L4-RN | VSD Fault | RAF-L4-RN | SW03 | Level-7 | -
Vent Fans | VSD Speed Control |  |  |  |  | 1 | [5 empty] | Display Only | 60s |  | RAF-L4-RN-SW04 | Level-7 | RAF-L4-RN | VSD Speed Control | RAF-L4-RN | SW04 | Level-7 | -
| Sub Total | 0 | 0 | 0 | 0 | 4 | 0
| SAF-L4-EDS | DI | DO | AI | AO | HLI | Prog | Condition | Timing | Priority | Graphic Name | Functionality | Frequency | [8 empty] | VSD-SAF-L4-EDS
Vent Fans | Enable |  |  |  |  | 1 |  |  |  |  | SAF-L4-EDS | Display & Override | COV |  | SAF-L4-EDS-SW01 | Level-7 | SAF-L4-EDS | Enable | SAF-L4-EDS | SW01 | #REF! | -
Vent Fans | Status |  |  |  |  | 1 |  | Mismatch with enable | 60s | Critical |  | Display / Red on Alarm | COV |  | SAF-L4-EDS-SW02 | Level-7 | SAF-L4-EDS | Status | SAF-L4-EDS | SW02 | #REF! | -
Vent Fans | VSD Fault |  |  |  |  | 1 |  | Change Of State | 60s | Critical |  | Display / Red on Alarm | COV |  | SAF-L4-EDS-SW03 | Level-7 | SAF-L4-EDS | VSD Fault | SAF-L4-EDS | SW03 | #REF! | -
Vent Fans | VSD Speed Control |  |  |  |  | 1 | [5 empty] | Display Only | 60s |  | SAF-L4-EDS-SW04 | Level-7 | SAF-L4-EDS | VSD Speed Control | SAF-L4-EDS | SW04 | #REF! | -
| RAF-L4-EDS | DI | DO | AI | AO | HLI | Prog | Condition | Timing | Priority | Graphic Name | Functionality | Frequency | [8 empty] | VSD-RAF-L4-EDS
Vent Fans | Enable |  |  |  |  | 1 |  |  |  |  | RAF-L4-EDS | Display & Override | COV |  | RAF-L4-EDS-SW01 | Level-7 | RAF-L4-EDS | Enable | RAF-L4-EDS | SW01 | Level-7 | -
Vent Fans | Status |  |  |  |  | 1 |  | Mismatch with enable | 60s | Critical |  | Display / Red on Alarm | COV |  | RAF-L4-EDS-SW02 | Level-7 | RAF-L4-EDS | Status | RAF-L4-EDS | SW02 | Level-7 | -
Vent Fans | VSD Fault |  |  |  |  | 1 |  | Change Of State | 60s | Critical |  | Display / Red on Alarm | COV |  | RAF-L4-EDS-SW03 | Level-7 | RAF-L4-EDS | VSD Fault | RAF-L4-EDS | SW03 | Level-7 | -
Vent Fans | VSD Speed Control |  |  |  |  | 1 | [5 empty] | Display Only | 60s |  | RAF-L4-EDS-SW04 | Level-7 | RAF-L4-EDS | VSD Speed Control | RAF-L4-EDS | SW04 | Level-7 | -
| Sub Total | 0 | 0 | 0 | 0 | 4 | 0
Stairs
| SPF-01 | DI | DO | AI | AO | HLI | Prog | Condition | Timing | Priority | Graphic Name | Functionality | Frequency | [8 empty] | VSD-SPF-01
Smoke | Enable |  |  |  |  | 1 |  |  |  |  | SPF-01 | Display & Override | COV |  | SPF-01-SW01 | Level-7 | SPF-01 | Enable | SPF-01 | SW01 | Level-7 | -
Smoke | Status |  |  |  |  | 1 |  | Mismatch with enable | 60s | Critical |  | Display / Red on Alarm | COV |  | SPF-01-SW02 | Level-7 | SPF-01 | Status | SPF-01 | SW02 | Level-7 | -
Smoke | VSD Fault |  |  |  |  | 1 |  | Change Of State | 60s | Critical |  | Display / Red on Alarm | COV |  | SPF-01-SW03 | Level-7 | SPF-01 | VSD Fault | SPF-01 | SW03 | Level-7 | -
Smoke | VSD Speed Control |  |  |  |  | 1 | [5 empty] | Display Only | 60s |  | SPF-01-SW04 | Level-7 | SPF-01 | VSD Speed Control | SPF-01 | SW04 | Level-7 | -
Smoke | Static DP transducer |  |  | 2 | [13 empty] | Static DP transducer |  |  |  | QBM2030-1U | 2
| Sub Total | 0 | 0 | 2 | 0 | 4 | 0
Stairs
| SPF-02 | DI | DO | AI | AO | HLI | Prog | Condition | Timing | Priority | Graphic Name | Functionality | Frequency | [8 empty] | VSD-SPF-02
Smoke | Enable |  |  |  |  | 1 |  |  |  |  | SPF-02 | Display & Override | COV |  | SPF-02-SW01 | Level-7 | SPF-02 | Enable | SPF-02 | SW01 | Level-7 | -
Smoke | Status |  |  |  |  | 1 |  | Mismatch with enable | 60s | Critical |  | Display / Red on Alarm | COV |  | SPF-02-SW02 | Level-7 | SPF-02 | Status | SPF-02 | SW02 | Level-7 | -
Smoke | VSD Fault |  |  |  |  | 1 |  | Change Of State | 60s | Critical |  | Display / Red on Alarm | COV |  | SPF-02-SW03 | Level-7 | SPF-02 | VSD Fault | SPF-02 | SW03 | Level-7 | -
Smoke | VSD Speed Control |  |  |  |  | 1 | [5 empty] | Display Only | 60s |  | SPF-02-SW04 | Level-7 | SPF-02 | VSD Speed Control | SPF-02 | SW04 | Level-7 | -
Smoke | Static DP transducer |  |  | 2 | [13 empty] | Static DP transducer |  |  |  | QBM2030-1U | 2
| Sub Total | 0 | 0 | 2 | 0 | 4 | 0
| GEF-L4-01 | DI | DO | AI | AO | HLI | Prog | Condition | Timing | Priority | Graphic Name | Functionality | Frequency | [8 empty] | VSD-GEF-L4-01
Level-7 | Enable |  |  |  |  | 1 |  |  |  |  | GEF-L4-01 | Display & Override | COV |  | GEF-L4-01-SW01 | Level-7 | GEF-L4-01 | Enable | GEF-L4-01 | SW01 | Level-7 | -
Level-7 | Status |  |  |  |  | 1 |  | Mismatch with enable | 60s | Critical |  | Display / Red on Alarm | COV |  | GEF-L4-01-SW02 | Level-7 | GEF-L4-01 | Status | GEF-L4-01 | SW02 | Level-7 | -
Level-7 | VSD Fault |  |  |  |  | 1 |  | Change Of State | 60s | Critical |  | Display / Red on Alarm | COV |  | GEF-L4-01-SW03 | Level-7 | GEF-L4-01 | VSD Fault | GEF-L4-01 | SW03 | Level-7 | -
Level-7 | VSD Speed Control |  |  |  |  | 1 | [5 empty] | Display Only | 60s |  | GEF-L4-01-SW04 | Level-7 | GEF-L4-01 | VSD Speed Control | GEF-L4-01 | SW04 | Level-7 | -
| Sub Total | 0 | 0 | 0 | 0 | 4 | 0
Autopsy Room
| GEF-L4-02 | DI | DO | AI | AO | HLI | Prog | Condition | Timing | Priority | Graphic Name | Functionality | Frequency | [8 empty] | VSD-GEF-L4-02
Level-7 | Enable |  |  |  |  | 1 |  |  |  |  | GEF-L4-02 | Display & Override | COV |  | GEF-L4-02-SW01 | Level-7 | GEF-L4-02 | Enable | GEF-L4-02 | SW01 | Level-7 | -
Level-7 | Status |  |  |  |  | 1 |  | Mismatch with enable | 60s | Critical |  | Display / Red on Alarm | COV |  | GEF-L4-02-SW02 | Level-7 | GEF-L4-02 | Status | GEF-L4-02 | SW02 | Level-7 | -
Level-7 | VSD Fault |  |  |  |  | 1 |  | Change Of State | 60s | Critical |  | Display / Red on Alarm | COV |  | GEF-L4-02-SW03 | Level-7 | GEF-L4-02 | VSD Fault | GEF-L4-02 | SW03 | Level-7 | -
Level-7 | VSD Speed Control |  |  |  |  | 1 | [5 empty] | Display Only | 60s |  | GEF-L4-02-SW04 | Level-7 | GEF-L4-02 | VSD Speed Control | GEF-L4-02 | SW04 | Level-7 | -
| Sub Total | 0 | 0 | 0 | 0 | 4 | 0
EDS - Sanitary Compartments
| GEF-L4-03 | DI | DO | AI | AO | HLI | Prog | Condition | Timing | Priority | Graphic Name | Functionality | Frequency | [8 empty] | VSD-GEF-L4-03
Level-7 Plant | Enable |  |  |  |  | 1 |  |  |  |  | GEF-L4-03 | Display & Override | COV |  | GEF-L4-03-SW01 | Level-7 | GEF-L4-03 | Enable | GEF-L4-03 | SW01 | Level-7 | -
Level-7 Plant | Status |  |  |  |  | 1 |  | Mismatch with enable | 60s | Critical |  | Display / Red on Alarm | COV |  | GEF-L4-03-SW02 | Level-7 | GEF-L4-03 | Status | GEF-L4-03 | SW02 | Level-7 | -
Level-7 Plant | VSD Fault |  |  |  |  | 1 |  | Change Of State | 60s | Critical |  | Display / Red on Alarm | COV |  | GEF-L4-03-SW03 | Level-7 | GEF-L4-03 | VSD Fault | GEF-L4-03 | SW03 | Level-7 | -
Level-7 Plant | VSD Speed Control |  |  |  |  | 1 | [5 empty] | Display Only | 60s |  | GEF-L4-03-SW04 | Level-7 | GEF-L4-03 | VSD Speed Control | GEF-L4-03 | SW04 | Level-7 | -
| Sub Total | 0 | 0 | 0 | 0 | 4 | 0
Ambulance Loading Dock
| GEF-L4-05 | DI | DO | AI | AO | HLI | Prog | Condition | Timing | Priority | Graphic Name | Functionality | Frequency | [8 empty] | VSD-GEF-L4-05
Level-7 | Enable |  |  |  |  | 1 |  |  |  |  | GEF-L4-05 | Display & Override | COV |  | GEF-L4-05-SW01 | Level-7 | GEF-L4-05 | Enable | GEF-L4-05 | SW01 | Level-7 | -
Level-7 | Status |  |  |  |  | 1 |  | Mismatch with enable | 60s | Critical |  | Display / Red on Alarm | COV |  | GEF-L4-05-SW02 | Level-7 | GEF-L4-05 | Status | GEF-L4-05 | SW02 | Level-7 | -
Level-7 | VSD Fault |  |  |  |  | 1 |  | Change Of State | 60s | Critical |  | Display / Red on Alarm | COV |  | GEF-L4-05-SW03 | Level-7 | GEF-L4-05 | VSD Fault | GEF-L4-05 | SW03 | Level-7 | -
Level-7 | VSD Speed Control |  |  |  |  | 1 | [5 empty] | Display Only | 60s |  | GEF-L4-05-SW04 | Level-7 | GEF-L4-05 | VSD Speed Control | GEF-L4-05 | SW04 | Level-7 | -
| Sub Total | 0 | 0 | 0 | 0 | 4 | 0
Garbage
| GEF-L4/5/6/7 | DI | DO | AI | AO | HLI | Prog | Condition | Timing | Priority | Graphic Name | Functionality | Frequency | [8 empty] | VSD-GEF-L4 to L7
Level-7 | Enable |  |  |  |  | 1 |  |  |  |  | GEF-L4/5/6/7 | Display & Override | COV |  | GEF-L4/5/6/7-SW01 | Level-7 | GEF-L4/5/6/7 | Enable | GEF-L4/5/6/7 | SW01 | Level-7 | -
Level-7 | Status |  |  |  |  | 1 |  | Mismatch with enable | 60s | Critical |  | Display / Red on Alarm | COV |  | GEF-L4/5/6/7-SW02 | Level-7 | GEF-L4/5/6/7 | Status | GEF-L4/5/6/7 | SW02 | Level-7 | -
Level-7 | VSD Fault |  |  |  |  | 1 |  | Change Of State | 60s | Critical |  | Display / Red on Alarm | COV |  | GEF-L4/5/6/7-SW03 | Level-7 | GEF-L4/5/6/7 | VSD Fault | GEF-L4/5/6/7 | SW03 | Level-7 | -
Level-7 | VSD Speed Control |  |  |  |  | 1 | [5 empty] | Display Only | 60s |  | GEF-L4/5/6/7-SW04 | Level-7 | GEF-L4/5/6/7 | VSD Speed Control | GEF-L4/5/6/7 | SW04 | Level-7 | -
| Sub Total | 0 | 0 | 0 | 0 | 4 | 0
| GEF-L5-01 | DI | DO | AI | AO | HLI | Prog | Condition | Timing | Priority | Graphic Name | Functionality | Frequency | [8 empty] | VSD-GEF-L5-01
Level-7 | Enable |  |  |  |  | 1 |  |  |  |  | GEF-L5-01 | Display & Override | COV |  | GEF-L5-01-SW01 | Level-7 | GEF-L5-01 | Enable | GEF-L5-01 | SW01 | Level-7 | -
Level-7 | Status |  |  |  |  | 1 |  | Mismatch with enable | 60s | Critical |  | Display / Red on Alarm | COV |  | GEF-L5-01-SW02 | Level-7 | GEF-L5-01 | Status | GEF-L5-01 | SW02 | Level-7 | -
Level-7 | VSD Fault |  |  |  |  | 1 |  | Change Of State | 60s | Critical |  | Display / Red on Alarm | COV |  | GEF-L5-01-SW03 | Level-7 | GEF-L5-01 | VSD Fault | GEF-L5-01 | SW03 | Level-7 | -
Level-7 | VSD Speed Control |  |  |  |  | 1 | [5 empty] | Display Only | 60s |  | GEF-L5-01-SW04 | Level-7 | GEF-L5-01 | VSD Speed Control | GEF-L5-01 | SW04 | Level-7 | -
| Sub Total | 0 | 0 | 0 | 0 | 4 | 0
Isolation Room 1
| GEF-L5-02 | DI | DO | AI | AO | HLI | Prog | Condition | Timing | Priority | Graphic Name | Functionality | Frequency | [8 empty] | VSD-GEF-L5-02
Level-7 | Enable |  |  |  |  | 1 |  |  |  |  | GEF-L5-02 | Display & Override | COV |  | GEF-L5-02-SW01 | Level-7 | GEF-L5-02 | Enable | GEF-L5-02 | SW01 | Level-7 | -
Level-7 | Status |  |  |  |  | 1 |  | Mismatch with enable | 60s | Critical |  | Display / Red on Alarm | COV |  | GEF-L5-02-SW02 | Level-7 | GEF-L5-02 | Status | GEF-L5-02 | SW02 | Level-7 | -
Level-7 | VSD Fault |  |  |  |  | 1 |  | Change Of State | 60s | Critical |  | Display / Red on Alarm | COV |  | GEF-L5-02-SW03 | Level-7 | GEF-L5-02 | VSD Fault | GEF-L5-02 | SW03 | Level-7 | -
Level-7 | VSD Speed Control |  |  |  |  | 1 | [5 empty] | Display Only | 60s |  | GEF-L5-02-SW04 | Level-7 | GEF-L5-02 | VSD Speed Control | GEF-L5-02 | SW04 | Level-7 | -
| Sub Total | 0 | 0 | 0 | 0 | 4 | 0
Isolation Room 1
| GEF-L5-03 | DI | DO | AI | AO | HLI | Prog | Condition | Timing | Priority | Graphic Name | Functionality | Frequency | [8 empty] | VSD-GEF-L5-03
Level-7 | Enable |  |  |  |  | 1 |  |  |  |  | GEF-L5-03 | Display & Override | COV |  | GEF-L5-03-SW01 | Level-7 | GEF-L5-03 | Enable | GEF-L5-03 | SW01 | Level-7 | -
Level-7 | Status |  |  |  |  | 1 |  | Mismatch with enable | 60s | Critical |  | Display / Red on Alarm | COV |  | GEF-L5-03-SW02 | Level-7 | GEF-L5-03 | Status | GEF-L5-03 | SW02 | Level-7 | -
Level-7 | VSD Fault |  |  |  |  | 1 |  | Change Of State | 60s | Critical |  | Display / Red on Alarm | COV |  | GEF-L5-03-SW03 | Level-7 | GEF-L5-03 | VSD Fault | GEF-L5-03 | SW03 | Level-7 | -
Level-7 | VSD Speed Control |  |  |  |  | 1 | [5 empty] | Display Only | 60s |  | GEF-L5-03-SW04 | Level-7 | GEF-L5-03 | VSD Speed Control | GEF-L5-03 | SW04 | Level-7 | -
| Sub Total | 0 | 0 | 0 | 0 | 4 | 0
Isolation Room 2
| GEF-L5-04 | DI | DO | AI | AO | HLI | Prog | Condition | Timing | Priority | Graphic Name | Functionality | Frequency | [8 empty] | VSD-GEF-L5-04
Level-7 | Enable |  |  |  |  | 1 |  |  |  |  | GEF-L5-04 | Display & Override | COV |  | GEF-L5-04-SW01 | Level-7 | GEF-L5-04 | Enable | GEF-L5-04 | SW01 | Level-7 | -
Level-7 | Status |  |  |  |  | 1 |  | Mismatch with enable | 60s | Critical |  | Display / Red on Alarm | COV |  | GEF-L5-04-SW02 | Level-7 | GEF-L5-04 | Status | GEF-L5-04 | SW02 | Level-7 | -
Level-7 | VSD Fault |  |  |  |  | 1 |  | Change Of State | 60s | Critical |  | Display / Red on Alarm | COV |  | GEF-L5-04-SW03 | Level-7 | GEF-L5-04 | VSD Fault | GEF-L5-04 | SW03 | Level-7 | -
Level-7 | VSD Speed Control |  |  |  |  | 1 | [5 empty] | Display Only | 60s |  | GEF-L5-04-SW04 | Level-7 | GEF-L5-04 | VSD Speed Control | GEF-L5-04 | SW04 | Level-7 | -
Isolation Room 2
| Sub Total | 0 | 0 | 0 | 0 | 4 | 0
| GEF-L5-05 | DI | DO | AI | AO | HLI | Prog | Condition | Timing | Priority | Graphic Name | Functionality | Frequency | [8 empty] | VSD-GEF-L5-05
Level-7 | Enable |  |  |  |  | 1 |  |  |  |  | GEF-L5-05 | Display & Override | COV |  | GEF-L5-05-SW01 | Level-7 | GEF-L5-05 | Enable | GEF-L5-05 | SW01 | Level-7 | -
Level-7 | Status |  |  |  |  | 1 |  | Mismatch with enable | 60s | Critical |  | Display / Red on Alarm | COV |  | GEF-L5-05-SW02 | Level-7 | GEF-L5-05 | Status | GEF-L5-05 | SW02 | Level-7 | -
Level-7 | VSD Fault |  |  |  |  | 1 |  | Change Of State | 60s | Critical |  | Display / Red on Alarm | COV |  | GEF-L5-05-SW03 | Level-7 | GEF-L5-05 | VSD Fault | GEF-L5-05 | SW03 | Level-7 | -
Level-7 | VSD Speed Control |  |  |  |  | 1 | [5 empty] | Display Only | 60s |  | GEF-L5-05-SW04 | Level-7 | GEF-L5-05 | VSD Speed Control | GEF-L5-05 | SW04 | Level-7 | -
| Sub Total | 0 | 0 | 0 | 0 | 4 | 0
Chiller Plantroom
| GEF-L7-01 | DI | DO | AI | AO | HLI | Prog | Condition | Timing | Priority | Graphic Name | Functionality | Frequency | [8 empty] | VSD-GEF-L7-01
Level-7 | Enable |  |  |  |  | 1 |  |  |  |  | GEF-L7-01 | Display & Override | COV |  | GEF-L7-01-SW01 | Level-7 | GEF-L7-01 | Enable | GEF-L7-01 | SW01 | Level-7 | -
Level-7 | Status |  |  |  |  | 1 |  | Mismatch with enable | 60s | Critical |  | Display / Red on Alarm | COV |  | GEF-L7-01-SW02 | Level-7 | GEF-L7-01 | Status | GEF-L7-01 | SW02 | Level-7 | -
Level-7 | VSD Fault |  |  |  |  | 1 |  | Change Of State | 60s | Critical |  | Display / Red on Alarm | COV |  | GEF-L7-01-SW03 | Level-7 | GEF-L7-01 | VSD Fault | GEF-L7-01 | SW03 | Level-7 | -
Level-7 | VSD Speed Control |  |  |  |  | 1 | [5 empty] | Display Only | 60s |  | GEF-L7-01-SW04 | Level-7 | GEF-L7-01 | VSD Speed Control | GEF-L7-01 | SW04 | Level-7 | -
| Sub Total | 0 | 0 | 0 | 0 | 4 | 0
Chiller Plantroom
| OAF-L7-04 | DI | DO | AI | AO | HLI | Prog | Condition | Timing | Priority | Graphic Name | Functionality | Frequency | [8 empty] | VSD-OAF-L7-04
Level-7 | Enable |  |  |  |  | 1 |  |  |  |  | OAF-L7-04 | Display & Override | COV |  | OAF-L7-04-SW01 | Level-7 | OAF-L7-04 | Enable | OAF-L7-04 | SW01 | Level-7 | -
Level-7 | Status |  |  |  |  | 1 |  | Mismatch with enable | 60s | Critical |  | Display / Red on Alarm | COV |  | OAF-L7-04-SW02 | Level-7 | OAF-L7-04 | Status | OAF-L7-04 | SW02 | Level-7 | -
Level-7 | VSD Fault |  |  |  |  | 1 |  | Change Of State | 60s | Critical |  | Display / Red on Alarm | COV |  | OAF-L7-04-SW03 | Level-7 | OAF-L7-04 | VSD Fault | OAF-L7-04 | SW03 | Level-7 | -
Level-7 | VSD Speed Control |  |  |  |  | 1 | [5 empty] | Display Only | 60s |  | OAF-L7-04-SW04 | Level-7 | OAF-L7-04 | VSD Speed Control | OAF-L7-04 | SW04 | Level-7 | -
| Sub Total | 0 | 0 | 0 | 0 | 4 | 0
| GEF-L7-CR | DI | DO | AI | AO | HLI | Prog | Condition | Timing | Priority | Graphic Name | Functionality | Frequency | [8 empty] | VSD-OAF-L7-04
Level-7 | Enable |  |  |  |  | 1 |  |  |  |  | GEF-L7-CR | Display & Override | COV |  | GEF-L7-CR-SW01 | Level-7 | GEF-L7-CR | Enable | GEF-L7-CR | SW01 | Level-7 | -
Level-7 | Status |  |  |  |  | 1 |  | Mismatch with enable | 60s | Critical |  | Display / Red on Alarm | COV |  | GEF-L7-CR-SW02 | Level-7 | GEF-L7-CR | Status | GEF-L7-CR | SW02 | Level-7 | -
Level-7 | VSD Fault |  |  |  |  | 1 |  | Change Of State | 60s | Critical |  | Display / Red on Alarm | COV |  | GEF-L7-CR-SW03 | Level-7 | GEF-L7-CR | VSD Fault | GEF-L7-CR | SW03 | Level-7 | -
Level-7 | VSD Speed Control |  |  |  |  | 1 | [5 empty] | Display Only | 60s |  | GEF-L7-CR-SW04 | Level-7 | GEF-L7-CR | VSD Speed Control | GEF-L7-CR | SW04 | Level-7 | -
Cooling Plant
| CHW Plant | DI | DO | AI | AO | HLI | Prog | Condition | Timing | Priority | Graphic Name | Functionality | Frequency |  |  | L7 East BMS Panel | [5 empty] | ECB600 | 1
CHW Plant | Supply Water Temp |  |  |  |  | 1 |  |  |  |  | Chiller |  |  |  | HLI-SW-01 | Level-7 | HLI | Supply Water Temp | HLI | SW-01 | Chiller 1/2
CHW Plant | Return Water Temp |  |  |  |  | 1 | [8 empty] | HLI-SW-02 | Level-7 | HLI | Return Water Temp | HLI | SW-02 | Chiller 1/2
CHW Plant | Cooling demand |  |  |  |  | 1 | [8 empty] | HLI-SW-03 | Level-7 | HLI | Cooling demand | HLI | SW-03 | Chiller 1/2
CHW Plant | Setpoint |  |  |  |  | 1 | [8 empty] | HLI-SW-04 | Level-7 | HLI | Setpoint | HLI | SW-04 | Chiller 1/2
CHW Plant | Consumption |  |  |  |  | 1 | [8 empty] | HLI-SW-05 | Level-7 | HLI | Load Limiting | HLI | SW-05 | Chiller 1/2
CHW Plant | Faults |  |  |  |  | 1 | [8 empty] | HLI-SW-06 | Level-7 | HLI | Faults | HLI | SW-06 | Chiller 1/2 | -
CHW Plant | Current State |  |  |  |  | 1 | [8 empty] | HLI-SW-07 | Level-7 | HLI | Current State | HLI | SW-07 | Chiller 1/2 | -
CHW Plant | Current Load |  |  |  |  | 1 | [8 empty] | HLI-SW-08 | Level-7 | HLI | Current Load | HLI | SW-08 | Chiller 1/2 | -
CHW Plant | Load Limiting |  |  |  |  | 1 | [8 empty] | HLI-SW-09 | Level-7 | HLI | Load Limiting | HLI | SW-09 | Chiller 1/2
CHW Plant | Flow Status |  |  |  |  | 1 | [8 empty] | HLI-SW-10 | Level-7 | HLI | Flow Status | HLI | SW-10 | Chiller 1/2
CHW Plant | Head Pressure |  |  |  |  | 1 | [8 empty] | HLI-SW-11 | Level-7 | HLI | Head Pressure | HLI | SW-11 | Chiller 1/2
CHW Plant | Suction Pressure |  |  |  |  | 1 | [8 empty] | HLI-SW-12 | Level-7 | HLI | Suction Pressure | HLI | SW-12 | Chiller 1/2
CHW Plant | Energy Meter |  |  |  |  | 1 | [5 empty] | Display only | COV |  | Energy Meter-SW-13 | Level-7 | Energy Meter | Energy Meter | Energy Meter | SW-13 | Level-7 | Energy meter | 1
CHW Plant | IO-DIM6-1 |  |  | 1 | [7 empty] | Display & Override | 10 Min or > 5% COV |  |  | Level-7 |  | IO-DIM6-1 |  | UI-1 |  | IO-DIM6 | 1
CHW Plant | CHW-PP-01 Status | 1 | [5 empty] | Change Of State | 60s | Critical |  |  |  |  | CHW Plant-UI-1 | Level-7 | CHW Plant | CHW-PP-01 Status | CHW Plant |  | Level-7 | SFS-1 | 1
CHW Plant | CHW-PP-02 Status | 1 | [5 empty] | Change Of State | 60s | Critical | [5 empty] | Level-7 | CHW Plant | CHW-PP-02 Status | CHW Plant |  | Level-7 | SFS-1 | 1
CHW Plant | CHW-SP-01 Status | 1 | [5 empty] | Change Of State | 60s | Critical | [5 empty] | Level-7 | CHW Plant | CHW-SP-01 Status | CHW Plant |  | Level-7 | SFS-1 | 1
CHW Plant | CHW-SP-02 Status | 1 | [5 empty] | Change Of State | 60s | Critical | [5 empty] | Level-7 | CHW Plant | CHW-SP-02 Status | CHW Plant |  | Level-7 | SFS-1 | 1
CHW Plant | Chem Treatment Alarm 1 |  |  | 1 | [7 empty] | Display only | COV |  | CHW Plant-UI-4 | Level-7 | CHW Plant | Chem Treatment Alarm 1 | CHW Plant | UI-4 | Level-7 | Terminals | 1
CHW Plant | Chem Treatment Alarm 2 |  |  | 1 | [7 empty] | Display only | COV |  | CHW Plant-UI-4 | Level-7 | CHW Plant | Chem Treatment Alarm 2 | CHW Plant | UI-4 | Level-7 | Terminals | 1
CHW Plant | IO-DIM6-2 |  |  | 1 | [7 empty] | Display & Override | 10 Min or > 5% COV |  |  | Level-7 |  | IO-DIM6-2 |  | UI-2 |  | IO-DIM6 | 1
CHW Plant | CH1 Chiller Status | 1 | [5 empty] | Change Of State | 60s | Critical |  |  |  |  | CHW Plant- | Level-7 | CHW Plant | CH1 Chiller Status | CHW Plant |  | Level-7 | Terminals | 1
CHW Plant | CH2 Chiller Status | 1 | [5 empty] | Change Of State | 60s | Critical |  |  |  |  | CHW Plant- | Level-7 | CHW Plant | CH2 Chiller Status | CHW Plant |  | Level-7 | Terminals | 1
CHW Plant | CH1 Chiller General Fault | 1 | [5 empty] | Change Of State | 60s | Critical |  |  |  |  | CHW Plant- | Level-7 | CHW Plant | CH1 Chiller General Fault | CHW Plant |  | Level-7 | Terminals | 1
CHW Plant | CH2 Chiller General Fault | 1 | [5 empty] | Change Of State | 60s | Critical |  |  |  |  | CHW Plant- | Level-7 | CHW Plant | CH2 Chiller General Fault | CHW Plant |  | Level-7 | Terminals | 1
CHW Plant | Leak Detector CH1 |  |  | 1 | [7 empty] | Display only | COV |  | CHW Plant-UI-3 | Level-7 | CHW Plant | Leak Detector CH1 | CHW Plant | UI-3 | Level-7 | Terminals | 1
CHW Plant | Leak Detector CH2 |  |  | 1 | [7 empty] | Display only | COV |  | CHW Plant-UI-4 | Level-7 | CHW Plant | Leak Detector CH2 | CHW Plant | UI-4 | Level-7 | Terminals | 1
CHW Plant | Chiller 1 Evaporator DP |  |  | 1 |  |  |  | >or< Setpoint by 5% | 15min(1Hour Inhibit) | Critical |  | Display only | COV |  | CHW Plant-UI-5 | Level-7 | CHW Plant | Chiller 1 Evaporator DP | CHW Plant | UI-5 | Level-7 | QBE3000-D1 | 1
CHW Plant | Chiller 2 Evaporator DP |  |  | 1 |  |  |  | >or< Setpoint by 5% | 15min(1Hour Inhibit) | Critical |  | Display only | COV |  | CHW Plant-UI-6 | Level-7 | CHW Plant | Chiller 2 Evaporator DP | CHW Plant | UI-6 | Level-7 | QBE3000-D1 | 1
CHW Plant | System DP |  |  | 1 |  |  |  | >or< Setpoint by 5% | 15min(1Hour Inhibit) | Critical |  | Display only | COV |  | CHW Plant-UI-7 | Level-7 | CHW Plant | System DP | CHW Plant | UI-7 | Level-7 | QBE3000-D4 | 1
CHW Plant | Secondary CHW Flow |  |  | 1 | [7 empty] | Display only | COV |  | CHW Plant-UI-8 | Level-7 | CHW Plant | Secondary CHW Flow | CHW Plant | UI-8 | Level-7 | Flow meter | 1
CHW Plant | Decoupler CHW Flow |  |  | 1 | [7 empty] | Display only | COV |  | CHW Plant-UI-9 | Level-7 | CHW Plant | Decoupler CHW Flow | CHW Plant | UI-9 | Level-7 | Flow meter | 1
CHW Plant | Secondary CHW Supply Temp |  |  | 1 | [7 empty] | Display only | COV |  | CHW Plant-UI-10 | Level-7 | CHW Plant | Secondary CHW Supply Temp | CHW Plant | UI-10 | Level-7 | PDIGR-TE200CE24C2E + well | 1
CHW Plant | Secondary CHW Return Temp |  |  | 1 | [7 empty] | Display only | COV |  | CHW Plant-UI-11 | Level-7 | CHW Plant | Secondary CHW Return Temp | CHW Plant | UI-11 | Level-7 | PDIGR-TE200CE24C2E + well | 1
CHW Plant | Decoupler CHW Temp |  |  | 1 | [7 empty] | Display only | COV |  | CHW Plant-UI-12 | Level-7 | CHW Plant | Decoupler CHW Temp | CHW Plant | UI-12 | Level-7 | PDIGR-TE200CE24C2E + well | 1
CHW Plant | Tank Low CHW Temp | 1 | [5 empty] | Change Of State | 60s | Critical |  |  |  |  | CHW Plant-UI-13 | Level-7 | CHW Plant | Tank Low CHW Temp | CHW Plant | UI-13 | Level-7 | PDIGR-TE200CE24C2E + well | 1
CHW Plant | Tank High CHW Temp | 1 | [5 empty] | Change Of State | 60s | Critical |  |  |  |  | CHW Plant-UI-14 | Level-7 | CHW Plant | Tank High CHW Temp | CHW Plant | UI-14 | Level-7 | PDIGR-TE200CE24C2E + well | 1
CHW Plant | Chiller 1 Condenser DP | 1 | [5 empty] | Change Of State | 60s | Critical |  |  |  |  | CHW Plant-UI-15 | Level-7 | CHW Plant | Chiller 1 Condenser DP | CHW Plant | UI-15 | Level-7 | QBE3000-D1 | 1
CHW Plant | Chiller 2 Condenser DP | 1 | [5 empty] | Change Of State | 60s | Critical |  |  |  |  | CHW Plant-UI-16 | Level-7 | CHW Plant | Chiller 2 Condenser DP | CHW Plant | UI-16 | Level-7 | QBE3000-D1 | 1
Chiller Plantroom | CH1 Chiller Enable |  | 1 | [8 empty] | Display and Override | COV |  | CHW Plant-UO-1 | Level-7 | CHW Plant | CH1 Chiller Enable | CHW Plant | UO-1 | Level-7 | 12VDC Relay | 1
Chiller Plantroom | CH2 Chiller Enable |  | 1 | [8 empty] | Display and Override | COV |  | CHW Plant-UO-2 | Level-7 | CHW Plant | CH2 Chiller Enable | CHW Plant | UO-2 | Level-7 | 12VDC Relay | 1
CHW Plant | CHW Bypass Valve |  |  |  | 1 | [6 empty] | Display only | COV |  | CHW Plant-UO-3 | Level-7 | CHW Plant | CHW Bypass Valve | CHW Plant | UO-3 | Level-7 | CHWV Actuator | 1
| Sub Total | 12 | 2 | 14 | 1 | 13 | 0
| CHW Plant Extension | DI | DO | AI | AO | HLI | Prog | Condition | Timing | Priority | Graphic Name | Functionality | Frequency | [8 empty] | ECX400 | 1
CW & CTs | CW-P-01 Status | 1 | [12 empty] | CHW Plant-UI-1 | Level-7 | CHW Plant | CW-P-01 Status | CHW Plant | UI-1 | Level-7 | SFS-1 | 1
CW & CTs | CW-P-02 Status | 1 | [12 empty] | CHW Plant-UI-2 | Level-7 | CHW Plant | CW-P-02 Status | CHW Plant | UI-2 | Level-7 | SFS-1 | 1
CW & CTs | CT 1 Cell 1 Sump Temp |  |  | 1 | [7 empty] | Display only | COV |  | CHW Plant-UI-3 | Level-7 | CHW Plant | CT 1 Cell 1 Sump Temp | CHW Plant | UI-3 | Level-7 | PDIGR-TE200CE24C2E + well | 1
CW & CTs | CT 1 Cell 2 Sump Temp |  |  | 1 | [7 empty] | Display only | COV |  | CHW Plant-UI-4 | Level-7 | CHW Plant | CT 1 Cell 2 Sump Temp | CHW Plant | UI-4 | Level-7 | PDIGR-TE200CE24C2E + well | 1
CW & CTs | CT Common Leave Temp |  |  | 1 | [7 empty] | Display only | COV |  | CHW Plant-UI-5 | Level-7 | CHW Plant | CT Common Leave Temp | CHW Plant | UI-5 | Level-7 | PDIGR-TE200CE24C2E + well | 1
CW & CTs | CT1 Cell1 Enter CW Iso Valve |  |  |  | 1 |  |  | Change Of State | 60s | Critical |  | Display only | COV |  | CHW Plant-UO-1 | Level-7 | CHW Plant | CT1 Cell1 Enter CW Iso Valve | CHW Plant | UO-1 | Level-7 | CWV Actuator | 1
CW & CTs | CT1 Cell1 Leave CW Iso Valve |  |  |  | 1 |  |  | Change Of State | 60s | Critical |  | Display only | COV |  | CHW Plant-UO-2 | Level-7 | CHW Plant | CT1 Cell1 Leave CW Iso Valve | CHW Plant | UO-2 | Level-7 | CWV Actuator | 1
CW & CTs | CT1 Cell2 Enter CW Iso Valve |  |  |  | 1 |  |  | Change Of State | 60s | Critical |  | Display only | COV |  | CHW Plant-UO-3 | Level-7 | CHW Plant | CT1 Cell2 Enter CW Iso Valve | CHW Plant | UO-3 | Level-7 | CWV Actuator | 1
CW & CTs | CT1 Cell2 Leave CW Iso Valve |  |  |  | 1 |  |  | Change Of State | 60s | Critical |  | Display only | COV |  | CHW Plant-UO-4 | Level-7 | CHW Plant | CT1 Cell2 Leave CW Iso Valve | CHW Plant | UO-4 | Level-7 | CWV Actuator | 1
CW & CTs | CTs CW Bypass Valve |  |  |  | 1 |  |  | Change Of State | 60s | Critical |  | Display only | COV |  | CHW Plant-UO-5 | Level-7 | CHW Plant | CTs CW Bypass Valve | CHW Plant | UO-5 | Level-7 | CWV Actuator | 1
| Sub Total | 2 | 0 | 3 | 5 | 0 | 0
| CHW-SP-01 | DI | DO | AI | AO | HLI | Prog | Condition | Timing | Priority | Graphic Name | Functionality | Frequency | [8 empty] | VSD-CHW-SP-01
Pumps | Enable |  |  |  |  | 1 |  |  |  |  | CHW-SP-01 | Display & Override | COV |  | CHW-SP-01-SW01 | Level-7 | CHW-SP-01 | Enable | CHW-SP-01 | SW01 | Level-7 | -
Pumps | Status |  |  |  |  | 1 |  | Mismatch with enable | 60s | Critical |  | Display / Red on Alarm | COV |  | CHW-SP-01-SW02 | Level-7 | CHW-SP-01 | Status | CHW-SP-01 | SW02 | Level-7 | -
Pumps | VSD Fault |  |  |  |  | 1 |  | Change Of State | 60s | Critical |  | Display / Red on Alarm | COV |  | CHW-SP-01-SW03 | Level-7 | CHW-SP-01 | VSD Fault | CHW-SP-01 | SW03 | Level-7 | -
Pumps | VSD Speed Control |  |  |  |  | 1 | [5 empty] | Display Only | 60s |  | CHW-SP-01-SW04 | Level-7 | CHW-SP-01 | VSD Speed Control | CHW-SP-01 | SW04 | Level-7 | -
| Sub Total | 0 | 0 | 0 | 0 | 4 | 0
| CHW-SP-02 | DI | DO | AI | AO | HLI | Prog | Condition | Timing | Priority | Graphic Name | Functionality | Frequency | [8 empty] | VSD-CHW-SP-02
Pumps | Enable |  |  |  |  | 1 |  |  |  |  | CHW-SP-02 | Display & Override | COV |  | CHW-SP-02-SW01 | Level-7 | CHW-SP-02 | Enable | CHW-SP-02 | SW01 | Level-7 | -
Pumps | Status |  |  |  |  | 1 |  | Mismatch with enable | 60s | Critical |  | Display / Red on Alarm | COV |  | CHW-SP-02-SW02 | Level-7 | CHW-SP-02 | Status | CHW-SP-02 | SW02 | Level-7 | -
Pumps | VSD Fault |  |  |  |  | 1 |  | Change Of State | 60s | Critical |  | Display / Red on Alarm | COV |  | CHW-SP-02-SW03 | Level-7 | CHW-SP-02 | VSD Fault | CHW-SP-02 | SW03 | Level-7 | -
Pumps | VSD Speed Control |  |  |  |  | 1 | [5 empty] | Display Only | 60s |  | CHW-SP-02-SW04 | Level-7 | CHW-SP-02 | VSD Speed Control | CHW-SP-02 | SW04 | Level-7 | -
| Sub Total | 0 | 0 | 0 | 0 | 4 | 0
| CHW-PP-01 | DI | DO | AI | AO | HLI | Prog | Condition | Timing | Priority | Graphic Name | Functionality | Frequency | VSD- | [7 empty] | VSD-CHW-PP-01
Pumps | Enable |  |  |  |  | 1 |  |  |  |  | CHW-PP-01 | Display & Override | COV |  | CHW-PP-01-SW01 | Level-7 | CHW-PP-01 | Enable | CHW-PP-01 | SW01 | Level-7 | -
Pumps | Status |  |  |  |  | 1 |  | Mismatch with enable | 60s | Critical |  | Display / Red on Alarm | COV |  | CHW-PP-01-SW02 | Level-7 | CHW-PP-01 | Status | CHW-PP-01 | SW02 | Level-7 | -
Pumps | VSD Fault |  |  |  |  | 1 |  | Change Of State | 60s | Critical |  | Display / Red on Alarm | COV |  | CHW-PP-01-SW03 | Level-7 | CHW-PP-01 | VSD Fault | CHW-PP-01 | SW03 | Level-7 | -
Pumps | VSD Speed Control |  |  |  |  | 1 | [5 empty] | Display Only | 60s |  | CHW-PP-01-SW04 | Level-7 | CHW-PP-01 | VSD Speed Control | CHW-PP-01 | SW04 | Level-7 | -
| Sub Total | 0 | 0 | 0 | 0 | 4 | 0
| CHW-PP-02 | DI | DO | AI | AO | HLI | Prog | Condition | Timing | Priority | Graphic Name | Functionality | Frequency | [8 empty] | VSD-CHW-PP-02
Pumps | Enable |  |  |  |  | 1 |  |  |  |  | CHW-PP-02 | Display & Override | COV |  | CHW-PP-02-SW01 | Level-7 | CHW-PP-02 | Enable | CHW-PP-02 | SW01 | Level-7 | -
Pumps | Status |  |  |  |  | 1 |  | Mismatch with enable | 60s | Critical |  | Display / Red on Alarm | COV |  | CHW-PP-02-SW02 | Level-7 | CHW-PP-02 | Status | CHW-PP-02 | SW02 | Level-7 | -
Pumps | VSD Fault |  |  |  |  | 1 |  | Change Of State | 60s | Critical |  | Display / Red on Alarm | COV |  | CHW-PP-02-SW03 | Level-7 | CHW-PP-02 | VSD Fault | CHW-PP-02 | SW03 | Level-7 | -
Pumps | VSD Speed Control |  |  |  |  | 1 | [5 empty] | Display Only | 60s |  | CHW-PP-02-SW04 | Level-7 | CHW-PP-02 | VSD Speed Control | CHW-PP-02 | SW04 | Level-7 | -
| Sub Total | 0 | 0 | 0 | 0 | 4 | 0
| CW-P-01 | DI | DO | AI | AO | HLI | Prog | Condition | Timing | Priority | Graphic Name | Functionality | Frequency | [8 empty] | VSD-CW-P-01
Pumps | Enable |  |  |  |  | 1 |  |  |  |  | CW-P-01 | Display & Override | COV |  | CW-P-01-SW01 | Level-7 | CW-P-01 | Enable | CW-P-01 | SW01 | Level-7 | -
Pumps | Status |  |  |  |  | 1 |  | Mismatch with enable | 60s | Critical |  | Display / Red on Alarm | COV |  | CW-P-01-SW02 | Level-7 | CW-P-01 | Status | CW-P-01 | SW02 | Level-7 | -
Pumps | VSD Fault |  |  |  |  | 1 |  | Change Of State | 60s | Critical |  | Display / Red on Alarm | COV |  | CW-P-01-SW03 | Level-7 | CW-P-01 | VSD Fault | CW-P-01 | SW03 | Level-7 | -
Pumps | VSD Speed Control |  |  |  |  | 1 | [5 empty] | Display Only | 60s |  | CW-P-01-SW04 | Level-7 | CW-P-01 | VSD Speed Control | CW-P-01 | SW04 | Level-7 | -
| Sub Total | 0 | 0 | 0 | 0 | 4 | 0
| CW-P-02 | DI | DO | AI | AO | HLI | Prog | Condition | Timing | Priority | Graphic Name | Functionality | Frequency | [8 empty] | VSD-CW-P-02
Pumps | Enable |  |  |  |  | 1 |  |  |  |  | CW-P-02 | Display & Override | COV |  | CW-P-02-SW01 | Level-7 | CW-P-02 | Enable | CW-P-02 | SW01 | Level-7 | -
Pumps | Status |  |  |  |  | 1 |  | Mismatch with enable | 60s | Critical |  | Display / Red on Alarm | COV |  | CW-P-02-SW02 | Level-7 | CW-P-02 | Status | CW-P-02 | SW02 | Level-7 | -
Pumps | VSD Fault |  |  |  |  | 1 |  | Change Of State | 60s | Critical |  | Display / Red on Alarm | COV |  | CW-P-02-SW03 | Level-7 | CW-P-02 | VSD Fault | CW-P-02 | SW03 | Level-7 | -
Pumps | VSD Speed Control |  |  |  |  | 1 | [5 empty] | Display Only | 60s |  | CW-P-02-SW04 | Level-7 | CW-P-02 | VSD Speed Control | CW-P-02 | SW04 | Level-7 | -
[12 empty] | Display Only | 60s |  | - |  | 0 |  |  |  |  | -
| Sub Total | 0 | 0 | 0 | 0 | 4 | 0
| CT-F-01 | DI | DO | AI | AO | HLI | Prog | Condition | Timing | Priority | Graphic Name | Functionality | Frequency | [8 empty] | VSD-CT-F-01
Pumps | Enable |  |  |  |  | 1 |  |  |  |  | CT-F-01 | Display & Override | COV |  | CT-F-01-SW01 | Level-7 | CT-F-01 | Enable | CT-F-01 | SW01 | Level-7 | -
Pumps | Status |  |  |  |  | 1 |  | Mismatch with enable | 60s | Critical |  | Display / Red on Alarm | COV |  | CT-F-01-SW02 | Level-7 | CT-F-01 | Status | CT-F-01 | SW02 | Level-7 | -
Pumps | VSD Fault |  |  |  |  | 1 |  | Change Of State | 60s | Critical |  | Display / Red on Alarm | COV |  | CT-F-01-SW03 | Level-7 | CT-F-01 | VSD Fault | CT-F-01 | SW03 | Level-7 | -
Pumps | VSD Speed Control |  |  |  |  | 1 | [5 empty] | Display Only | 60s |  | CT-F-01-SW04 | Level-7 | CT-F-01 | VSD Speed Control | CT-F-01 | SW04 | Level-7 | -
| Sub Total | 0 | 0 | 0 | 0 | 4 | 0
| CT-F-02 | DI | DO | AI | AO | HLI | Prog | Condition | Timing | Priority | Graphic Name | Functionality | Frequency | [8 empty] | VSD-CT-F-02
Pumps | Enable |  |  |  |  | 1 |  |  |  |  | CT-F-02 | Display & Override | COV |  | CT-F-02-SW01 | Level-7 | CT-F-02 | Enable | CT-F-02 | SW01 | Level-7 | -
Pumps | Status |  |  |  |  | 1 |  | Mismatch with enable | 60s | Critical |  | Display / Red on Alarm | COV |  | CT-F-02-SW02 | Level-7 | CT-F-02 | Status | CT-F-02 | SW02 | Level-7 | -
Pumps | VSD Fault |  |  |  |  | 1 |  | Change Of State | 60s | Critical |  | Display / Red on Alarm | COV |  | CT-F-02-SW03 | Level-7 | CT-F-02 | VSD Fault | CT-F-02 | SW03 | Level-7 | -
Pumps | VSD Speed Control |  |  |  |  | 1 | [5 empty] | Display Only | 60s |  | CT-F-02-SW04 | Level-7 | CT-F-02 | VSD Speed Control | CT-F-02 | SW04 | Level-7 | -
| Sub Total | 0 | 0 | 0 | 0 | 4 | 0
Heating Plant
| HW Plant | DI | DO | AI | AO | HLI | Prog | Condition | Timing | Priority | Graphic Name | Functionality | Frequency |  |  | L7 HWG Panel | [5 empty] | ECB600 | 1
HW Plant | HW-PP-01 Status | 1 | [5 empty] | Change Of State | 60s | Critical |  |  |  |  | HW Plant -UI-1 | Level-7 | HW Plant | HW-PP-01 Status | HW Plant | UI-1 | Level-7 | SFS-1 | 1
HW Plant | HW-PP-02 Status | 1 | [5 empty] | Change Of State | 60s | Critical |  |  |  |  | HW Plant -UI-2 | Level-7 | HW Plant | HW-PP-02 Status | HW Plant | UI-2 | Level-7 | SFS-1 | 1
HW Plant | HW-SP-01 Status | 1 | [5 empty] | Change Of State | 60s | Critical |  |  |  |  | HW Plant -UI-3 | Level-7 | HW Plant | HW-SP-01 Status | HW Plant | UI-3 | Level-7 | SFS-1 | 1
HW Plant | HW-SP-02 Status | 1 | [5 empty] | Change Of State | 60s | Critical |  |  |  |  | HW Plant -UI-4 | Level-7 | HW Plant | HW-SP-02 Status | HW Plant | UI-4 | Level-7 | SFS-1 | 1
HW Plant | Boiler 1 DP |  |  | 1 |  |  |  | >or< Setpoint by 5% | 15min(1Hour Inhibit) | Critical |  | Display only | COV |  | HW Plant -UI-5 | Level-7 | HW Plant | Boiler 1 DP | HW Plant | UI-5 | Level-7 | QBE3000-D1 | 1
HW Plant | Boiler 2 DP |  |  | 1 |  |  |  | >or< Setpoint by 5% | 15min(1Hour Inhibit) | Critical |  | Display only | COV |  | HW Plant -UI-6 | Level-7 | HW Plant | Boiler 2 DP | HW Plant | UI-6 | Level-7 | QBE3000-D1 | 1
HW Plant | System DP |  |  | 1 |  |  |  | >or< Setpoint by 5% | 15min(1Hour Inhibit) | Critical |  | Display only | COV |  | HW Plant -UI-7 | Level-7 | HW Plant | System DP | HW Plant | UI-7 | Level-7 | QBE3000-D4 | 1
HW Plant | Secondary HW Flow |  |  | 1 | [7 empty] | Display only | COV |  | HW Plant -UI-8 | Level-7 | HW Plant | Secondary HW Flow | HW Plant | UI-8 | Level-7 | Flow meter | 1
HW Plant | Decoupler HW Flow |  |  | 1 | [7 empty] | Display only | COV |  | HW Plant -UI-9 | Level-7 | HW Plant | Decoupler HW Flow | HW Plant | UI-9 | Level-7 | Flow meter | 1
HW Plant | Secondary HW Supply Temp |  |  | 1 | [7 empty] | Display only | COV |  | HW Plant -UI-10 | Level-7 | HW Plant | Secondary HW Supply Temp | HW Plant | UI-10 | Level-7 | PDIGR-TE200CE24C2E + well | 1
HW Plant | Decoupler HW Temp |  |  | 1 | [7 empty] | Display only | COV |  | HW Plant -UI-11 | Level-7 | HW Plant | Decoupler HW Temp | HW Plant | UI-11 | Level-7 | PDIGR-TE200CE24C2E + well | 1
HW Plant | Secondary HW Return Temp |  |  | 1 | [7 empty] | Display only | COV |  | HW Plant -UI-14 | Level-7 | HW Plant | Secondary HW Return Temp | HW Plant | UI-14 | Level-7 | PDIGR-TE200CE24C2E + well | 1
HW Plant | Gas Solenoid Valve Interlock | 1 | [5 empty] | Change Of State | 60s | Critical |  |  |  |  | HW Plant -UI-15 | Level-7 | HW Plant | Gas Solenoid Valve Interlock | HW Plant | UI-15 | Level-7 | Terminals | 1
HW Plant | Bypass Valve |  |  |  | 1 | [6 empty] | Display only | COV |  | HW Plant -UO-1 | Level-7 | HW Plant | Bypass Valve | HW Plant | UO-1 | Level-7 | CHWV Actuator | 1
HW Plant | Boiler 1 Enable |  | 1 | [11 empty] | HW Plant -UO-2 | Level-7 | HW Plant | Boiler 1 Enable | HW Plant | UO-2 | Level-7 | 12VDC Relay
HW Plant | Boiler 2 Enable |  | 1 | [11 empty] | HW Plant -UO-3 | Level-7 | HW Plant | Boiler 2 Enable | HW Plant | UO-3 | Level-7 | 12VDC Relay
HW Plant | Boiler 1 Setpoint |  |  |  | 1 | [9 empty] | HW Plant -UO-4 | Level-7 | HW Plant | Boiler 1 Setpoint | HW Plant | UO-4 | Level-7 | Terminals
HW Plant | Boiler 2 Setpoint |  |  |  | 1 | [9 empty] | HW Plant -UO-5 | Level-7 | HW Plant | Boiler 2 Setpoint | HW Plant | UO-5 | Level-7 | Terminals
| Sub Total | 5 | 2 | 8 | 3 | 0 | 0
| HW Plant IO Expansion | DI | DO | AI | AO | HLI | Prog | Condition | Timing | Priority | Graphic Name | Functionality | Frequency | [8 empty] | ECX420 | 1
HW Plant | Boiler 1 Supply Water Temp |  |  | 1 | [10 empty] | HW Plant -UI-1 | Level-7 | HW Plant IO Expansion | Boiler 1 Supply Water Temp | HW Plant | UI-1 | Level-7 | PDIGR-TE200CE24C2E + well | 1
HW Plant | Boiler 1 Return Water Temp |  |  | 1 | [10 empty] | HW Plant -UI-2 | Level-7 | HW Plant IO Expansion | Boiler 1 Return Water Temp | HW Plant | UI-2 | Level-7 | PDIGR-TE200CE24C2E + well | 1
HW Plant | Boiler 1 Flow Status | 1 | [12 empty] | HW Plant -UI-3 | Level-7 | HW Plant IO Expansion | Boiler 1 Flow Status | HW Plant | UI-3 | Level-7 | Terminals | 1
HW Plant | Boiler 1 Fault | 1 | [12 empty] | HW Plant -UI-4 | Level-7 | HW Plant IO Expansion | Boiler 1 Fault | HW Plant | UI-4 | Level-7 | Terminals | 1
HW Plant | Boiler 2 Supply Water Temp |  |  | 1 | [10 empty] | HW Plant -UI-5 | Level-7 | HW Plant IO Expansion | Boiler 2 Supply Water Temp | HW Plant | UI-5 | Level-7 | PDIGR-TE200CE24C2E + well | 1
HW Plant | Boiler 2 Return Water Temp |  |  | 1 | [10 empty] | HW Plant -UI-6 | Level-7 | HW Plant IO Expansion | Boiler 2 Return Water Temp | HW Plant | UI-6 | Level-7 | PDIGR-TE200CE24C2E + well | 1
HW Plant | Boiler 2 Flow Status | 1 | [12 empty] | HW Plant -UI-7 | Level-7 | HW Plant IO Expansion | Boiler 2 Flow Status | HW Plant | UI-7 | Level-7 | Terminals | 1
HW Plant | Boiler 2 Fault | 1 | [12 empty] | HW Plant -UI-8 | Level-7 | HW Plant IO Expansion | Boiler 2 Fault | HW Plant | UI-8 | Level-7 | Terminals | 1
HW Plant | Boiler 1 A/O/M Switch Auto | 1 | [12 empty] | HW Plant -UI-9 | Level-7 | HW Plant IO Expansion | Boiler 1 A/O/M Switch Auto | HW Plant | UI-9 | Level-7 | Terminals | 1
HW Plant | Boiler 1 A/O/M Switch Manual | 1 | [12 empty] | HW Plant -UI-10 | Level-7 | HW Plant IO Expansion | Boiler 1 A/O/M Switch Manual | HW Plant | UI-10 | Level-7 | Terminals | 1
HW Plant | Boiler 2 A/O/M Switch Auto | 1 | [12 empty] | HW Plant -UI-11 | Level-7 | HW Plant IO Expansion | Boiler 2 A/O/M Switch Auto | HW Plant | UI-11 | Level-7 | Terminals | 1
HW Plant | Boiler 2 A/O/M Switch Manual | 1 | [12 empty] | HW Plant -UI-12 | Level-7 | HW Plant IO Expansion | Boiler 2 A/O/M Switch Manual | HW Plant | UI-12 | Level-7 | Terminals | 1
| Sub Total | 8 | 0 | 4 | 0 | 0 | 0
| HHW-SP-01 | DI | DO | AI | AO | HLI | Prog | Condition | Timing | Priority | Graphic Name | Functionality | Frequency | [8 empty] | VSD-HHW-SP-01
Pumps | Enable |  |  |  |  | 1 |  |  |  |  | HHW-SP-01 | Display & Override | COV |  | HHW-SP-01-SW01 | Level-7 | HHW-SP-01 | Enable | HHW-SP-01 | SW01 | Level-7 | -
Pumps | Status |  |  |  |  | 1 |  | Mismatch with enable | 60s | Critical |  | Display / Red on Alarm | COV |  | HHW-SP-01-SW02 | Level-7 | HHW-SP-01 | Status | HHW-SP-01 | SW02 | Level-7 | -
Pumps | VSD Fault |  |  |  |  | 1 |  | Change Of State | 60s | Critical |  | Display / Red on Alarm | COV |  | HHW-SP-01-SW03 | Level-7 | HHW-SP-01 | VSD Fault | HHW-SP-01 | SW03 | Level-7 | -
Pumps | VSD Speed Control |  |  |  |  | 1 | [5 empty] | Display Only | 60s |  | HHW-SP-01-SW04 | Level-7 | HHW-SP-01 | VSD Speed Control | HHW-SP-01 | SW04 | Level-7 | -
| Sub Total | 0 | 0 | 0 | 0 | 4 | 0
| HHW-SP-02 | DI | DO | AI | AO | HLI | Prog | Condition | Timing | Priority | Graphic Name | Functionality | Frequency | [8 empty] | VSD-HHW-SP-02
Pumps | Enable |  |  |  |  | 1 |  |  |  |  | HHW-SP-02 | Display & Override | COV |  | HHW-SP-02-SW01 | Level-7 | HHW-SP-02 | Enable | HHW-SP-02 | SW01 | Level-7 | -
Pumps | Status |  |  |  |  | 1 |  | Mismatch with enable | 60s | Critical |  | Display / Red on Alarm | COV |  | HHW-SP-02-SW02 | Level-7 | HHW-SP-02 | Status | HHW-SP-02 | SW02 | Level-7 | -
Pumps | VSD Fault |  |  |  |  | 1 |  | Change Of State | 60s | Critical |  | Display / Red on Alarm | COV |  | HHW-SP-02-SW03 | Level-7 | HHW-SP-02 | VSD Fault | HHW-SP-02 | SW03 | Level-7 | -
Pumps | VSD Speed Control |  |  |  |  | 1 | [5 empty] | Display Only | 60s |  | HHW-SP-02-SW04 | Level-7 | HHW-SP-02 | VSD Speed Control | HHW-SP-02 | SW04 | Level-7 | -
| Sub Total | 0 | 0 | 0 | 0 | 4 | 0
| HHW-PP-01 | DI | DO | AI | AO | HLI | Prog | Condition | Timing | Priority | Graphic Name | Functionality | Frequency | [8 empty] | VSD-HHW-PP-01
Pumps | Enable |  |  |  |  | 1 |  |  |  |  | HHW-PP-01 | Display & Override | COV |  | HHW-PP-01-SW01 | Level-7 | HHW-PP-01 | Enable | HHW-PP-01 | SW01 | Level-7 | -
Pumps | Status |  |  |  |  | 1 |  | Mismatch with enable | 60s | Critical |  | Display / Red on Alarm | COV |  | HHW-PP-01-SW02 | Level-7 | HHW-PP-01 | Status | HHW-PP-01 | SW02 | Level-7 | -
Pumps | VSD Fault |  |  |  |  | 1 |  | Change Of State | 60s | Critical |  | Display / Red on Alarm | COV |  | HHW-PP-01-SW03 | Level-7 | HHW-PP-01 | VSD Fault | HHW-PP-01 | SW03 | Level-7 | -
Pumps | VSD Speed Control |  |  |  |  | 1 | [5 empty] | Display Only | 60s |  | HHW-PP-01-SW04 | Level-7 | HHW-PP-01 | VSD Speed Control | HHW-PP-01 | SW04 | Level-7 | -
| Sub Total | 0 | 0 | 0 | 0 | 4 | 0
| HHW-PP-02 | DI | DO | AI | AO | HLI | Prog | Condition | Timing | Priority | Graphic Name | Functionality | Frequency | [8 empty] | VSD-HHW-PP-02
Pumps | Enable |  |  |  |  | 1 |  |  |  |  | HHW-PP-02 | Display & Override | COV |  | HHW-PP-02-SW01 | Level-7 | HHW-PP-02 | Enable | HHW-PP-02 | SW01 | Level-7 | -
Pumps | Status |  |  |  |  | 1 |  | Mismatch with enable | 60s | Critical |  | Display / Red on Alarm | COV |  | HHW-PP-02-SW02 | Level-7 | HHW-PP-02 | Status | HHW-PP-02 | SW02 | Level-7 | -
Pumps | VSD Fault |  |  |  |  | 1 |  | Change Of State | 60s | Critical |  | Display / Red on Alarm | COV |  | HHW-PP-02-SW03 | Level-7 | HHW-PP-02 | VSD Fault | HHW-PP-02 | SW03 | Level-7 | -
Pumps | VSD Speed Control |  |  |  |  | 1 | [5 empty] | Display Only | 60s |  | HHW-PP-02-SW04 | Level-7 | HHW-PP-02 | VSD Speed Control | HHW-PP-02 | SW04 | Level-7 | -
| Sub Total | 0 | 0 | 0 | 0 | 4 | 0
Note on W15: Mike Walsh: Actuator Part Number
Note on W30: Mike Walsh: Actuator Part Number
Note on W31: Mike Walsh: Actuator Part Number
Note on W42: Mike Walsh: Actuator Part Number
Note on W43: Mike Walsh: Actuator Part Number
Note on W54: Mike Walsh: Actuator Part Number
Note on W55: Mike Walsh: Actuator Part Number
Note on W56: Mike Walsh: Actuator Part Number
Note on W68: Mike Walsh: Actuator Part Number
Note on W69: Mike Walsh: Actuator Part Number
Note on W70: Mike Walsh: Actuator Part Number
Note on W80: Mike Walsh: Actuator Part Number
Note on W81: Mike Walsh: Actuator Part Number
Note on W82: Mike Walsh: Actuator Part Number
Note on W111: Mike Walsh: Actuator Part Number
Note on W112: Mike Walsh: Actuator Part Number
Note on W119: Mike Walsh: Actuator Part Number
Note on W120: Mike Walsh: Actuator Part Number
Note on W127: Mike Walsh: Actuator Part Number
Note on W128: Mike Walsh: Actuator Part Number
Note on W135: Mike Walsh: Actuator Part Number
Note on W136: Mike Walsh: Actuator Part Number
Note on W143: Mike Walsh: Actuator Part Number
Note on W144: Mike Walsh: Actuator Part Number
Note on W151: Mike Walsh: Actuator Part Number
Note on W152: Mike Walsh: Actuator Part Number
Note on W159: Mike Walsh: Actuator Part Number
Note on W160: Mike Walsh: Actuator Part Number
Note on W167: Mike Walsh: Actuator Part Number
Note on W168: Mike Walsh: Actuator Part Number
Note on W175: Mike Walsh: Actuator Part Number
Note on W176: Mike Walsh: Actuator Part Number
Note on W183: Mike Walsh: Actuator Part Number
Note on W184: Mike Walsh: Actuator Part Number
Note on W191: Mike Walsh: Actuator Part Number
Note on W192: Mike Walsh: Actuator Part Number
Note on W199: Mike Walsh: Actuator Part Number
Note on W200: Mike Walsh: Actuator Part Number
Note on W209: Mike Walsh: Actuator Part Number
Note on W210: Mike Walsh: Actuator Part Number
Note on W217: Mike Walsh: Actuator Part Number
Note on W218: Mike Walsh: Actuator Part Number
Note on W225: Mike Walsh: Actuator Part Number
Note on W226: Mike Walsh: Actuator Part Number
Note on W233: Mike Walsh: Actuator Part Number
Note on W234: Mike Walsh: Actuator Part Number
Note on W241: Mike Walsh: Actuator Part Number
Note on W242: Mike Walsh: Actuator Part Number
Note on W249: Mike Walsh: Actuator Part Number
Note on W250: Mike Walsh: Actuator Part Number
Note on W257: Mike Walsh: Actuator Part Number
Note on W258: Mike Walsh: Actuator Part Number
Note on W265: Mike Walsh: Actuator Part Number
Note on W266: Mike Walsh: Actuator Part Number
Note on W273: Mike Walsh: Actuator Part Number
Note on W274: Mike Walsh: Actuator Part Number
Note on W281: Mike Walsh: Actuator Part Number
Note on W282: Mike Walsh: Actuator Part Number
Note on W289: Mike Walsh: Actuator Part Number
Note on W290: Mike Walsh: Actuator Part Number
Note on W297: Mike Walsh: Actuator Part Number
Note on W306: Mike Walsh: Actuator Part Number
Note on W314: Mike Walsh: Actuator Part Number
Note on W322: Mike Walsh: Actuator Part Number
Note on W337: Mike Walsh: Actuator Part Number
Note on W345: Mike Walsh: Actuator Part Number
Note on W353: Mike Walsh: Actuator Part Number
Note on W361: Mike Walsh: Actuator Part Number
Note on W369: Mike Walsh: Actuator Part Number
Note on W377: Mike Walsh: Actuator Part Number
Note on W385: Mike Walsh: Actuator Part Number
Note on W392: Mike Walsh: Actuator Part Number
Note on W400: Mike Walsh: Actuator Part Number
Note on W424: Mike Walsh: Actuator Part Number
Note on W425: Mike Walsh: Actuator Part Number
Note on W439: Mike Walsh: Actuator Part Number
Note on W440: Mike Walsh: Actuator Part Number
Note on W450: Mike Walsh: Actuator Part Number
Note on W451: Mike Walsh: Actuator Part Number
Note on W452: Mike Walsh: Actuator Part Number
Note on W464: Mike Walsh: Actuator Part Number
Note on W465: Mike Walsh: Actuator Part Number
Note on W480: Mike Walsh: Actuator Part Number
Note on W481: Mike Walsh: Actuator Part Number
Note on W494: Mike Walsh: Actuator Part Number
Note on W495: Mike Walsh: Actuator Part Number
Note on W509: Mike Walsh: Actuator Part Number
Note on W510: Mike Walsh: Actuator Part Number
Note on W522: Mike Walsh: Actuator Part Number
Note on W523: Mike Walsh: Actuator Part Number
Note on W537: Mike Walsh: Actuator Part Number
Note on W538: Mike Walsh: Actuator Part Number
Note on W548: Mike Walsh: Actuator Part Number
Note on W549: Mike Walsh: Actuator Part Number
Note on W561: Mike Walsh: Actuator Part Number
Note on W562: Mike Walsh: Actuator Part Number
Note on W576: Mike Walsh: Actuator Part Number
Note on W577: Mike Walsh: Actuator Part Number
Note on W578: Mike Walsh: Actuator Part Number
Note on W588: Mike Walsh: Actuator Part Number
Note on W589: Mike Walsh: Actuator Part Number
Note on W600: Mike Walsh: Actuator Part Number
Note on W601: Mike Walsh: Actuator Part Number
Note on W610: Mike Walsh: Actuator Part Number
Note on W611: Mike Walsh: Actuator Part Number
Note on W612: Mike Walsh: Actuator Part Number
Note on W626: Mike Walsh: Actuator Part Number
Note on W627: Mike Walsh: Actuator Part Number
Note on W652: Mike Walsh: Actuator Part Number
Note on W653: Mike Walsh: Actuator Part Number
Note on W670: Mike Walsh: Actuator Part Number
Note on W671: Mike Walsh: Actuator Part Number
Note on W685: Mike Walsh: Actuator Part Number
Note on W686: Mike Walsh: Actuator Part Number
Note on W697: Mike Walsh: Actuator Part Number
Note on W698: Mike Walsh: Actuator Part Number
Note on W708: Mike Walsh: Actuator Part Number
Note on W709: Mike Walsh: Actuator Part Number
Note on W721: Mike Walsh: Actuator Part Number
Note on W722: Mike Walsh: Actuator Part Number
Note on W741: Mike Walsh: Actuator Part Number
Note on W742: Mike Walsh: Actuator Part Number
Note on W757: Mike Walsh: Actuator Part Number
Note on W758: Mike Walsh: Actuator Part Number
Note on W759: Mike Walsh: Actuator Part Number
Note on W774: Mike Walsh: Actuator Part Number
Note on W775: Mike Walsh: Actuator Part Number
Note on W776: Mike Walsh: Actuator Part Number
Note on W777: Mike Walsh: Actuator Part Number
Note on W797: Mike Walsh: Actuator Part Number
Note on W798: Mike Walsh: Actuator Part Number
Note on W799: Mike Walsh: Actuator Part Number
Note on W800: Mike Walsh: Actuator Part Number
Note on W801: Mike Walsh: Actuator Part Number
Note on W817: Mike Walsh: Actuator Part Number
Note on W818: Mike Walsh: Actuator Part Number
Note on W819: Mike Walsh: Actuator Part Number
Note on W833: Mike Walsh: Actuator Part Number
Note on W843: Mike Walsh: Actuator Part Number
Note on W844: Mike Walsh: Actuator Part Number
Note on W854: Mike Walsh: Actuator Part Number
Note on W855: Mike Walsh: Actuator Part Number
Note on W867: Mike Walsh: Actuator Part Number
Note on W868: Mike Walsh: Actuator Part Number
Note on W928: Mike Walsh: Actuator Part Number
Note on W929: Mike Walsh: Actuator Part Number
Note on W930: Mike Walsh: Actuator Part Number
Note on W931: Mike Walsh: Actuator Part Number
Note on W936: Mike Walsh: Actuator Part Number
Note on W937: Mike Walsh: Actuator Part Number
Note on W938: Mike Walsh: Actuator Part Number
Note on W939: Mike Walsh: Actuator Part Number
Note on W953: Mike Walsh: Actuator Part Number
Note on W954: Mike Walsh: Actuator Part Number
Note on W955: Mike Walsh: Actuator Part Number
Note on W956: Mike Walsh: Actuator Part Number
Note on W961: Mike Walsh: Actuator Part Number
Note on W962: Mike Walsh: Actuator Part Number
Note on W963: Mike Walsh: Actuator Part Number
Note on W964: Mike Walsh: Actuator Part Number
Note on W1002: Mike Walsh: Actuator Part Number
Note on W1003: Mike Walsh: Actuator Part Number
Note on W1004: Mike Walsh: Actuator Part Number
Note on W1005: Mike Walsh: Actuator Part Number
Note on W1010: Mike Walsh: Actuator Part Number
Note on W1011: Mike Walsh: Actuator Part Number
Note on W1012: Mike Walsh: Actuator Part Number
Note on W1013: Mike Walsh: Actuator Part Number
Note on W1024: Mike Walsh: Actuator Part Number
Note on W1025: Mike Walsh: Actuator Part Number
Note on W1026: Mike Walsh: Actuator Part Number
Note on W1027: Mike Walsh: Actuator Part Number
Note on W1028: Mike Walsh: Actuator Part Number
Note on W1029: Mike Walsh: Actuator Part Number
Note on W1032: Mike Walsh: Actuator Part Number
Note on W1033: Mike Walsh: Actuator Part Number
Note on W1067: Mike Walsh: Actuator Part Number
Note on W1075: Mike Walsh: Actuator Part Number
Note on W1178: Mike Walsh: Actuator Part Number
Note on W1179: Mike Walsh: Actuator Part Number
Note on W1180: Mike Walsh: Actuator Part Number
Note on W1181: Mike Walsh: Actuator Part Number
Note on W1182: Mike Walsh: Actuator Part Number
Note on W1183: Mike Walsh: Actuator Part Number
Note on W1184: Mike Walsh: Actuator Part Number
Note on W1185: Mike Walsh: Actuator Part Number
Note on W1186: Mike Walsh: Actuator Part Number
Note on W1187: Mike Walsh: Actuator Part Number
Note on W1190: Mike Walsh: Actuator Part Number
Note on W1191: Mike Walsh: Actuator Part Number
Note on W1192: Mike Walsh: Actuator Part Number
Note on W1193: Mike Walsh: Actuator Part Number
Note on W1194: Mike Walsh: Actuator Part Number
Note on W1197: Mike Walsh: Actuator Part Number
Note on W1198: Mike Walsh: Actuator Part Number
Note on W1199: Mike Walsh: Actuator Part Number
Note on W1200: Mike Walsh: Actuator Part Number
Note on W1201: Mike Walsh: Actuator Part Number
Note on W1207: Mike Walsh: Actuator Part Number
Note on W1208: Mike Walsh: Actuator Part Number
Note on W1211: Mike Walsh: Actuator Part Number
Note on W1215: Mike Walsh: Actuator Part Number
Note on W1216: Mike Walsh: Actuator Part Number
Note on W1220: Mike Walsh: Actuator Part Number
Note on W1221: Mike Walsh: Actuator Part Number
Note on W1222: Mike Walsh: Actuator Part Number
Note on W1223: Mike Walsh: Actuator Part Number
Note on W1224: Mike Walsh: Actuator Part Number
Note on W1288: Mike Walsh: Actuator Part Number
Note on W1289: Mike Walsh: Actuator Part Number
Note on W1290: Mike Walsh: Actuator Part Number
Note on W1291: Mike Walsh: Actuator Part Number
Note on W1292: Mike Walsh: Actuator Part Number
Note on W1293: Mike Walsh: Actuator Part Number
Note on W1294: Mike Walsh: Actuator Part Number
Note on W1295: Mike Walsh: Actuator Part Number
Note on W1296: Mike Walsh: Actuator Part Number
Note on W1301: Mike Walsh: Actuator Part Number

## Sheet1
Cooling Plant
| CHW Plant | DI | DO | AI | AO | HLI | Prog | Condition | Timing | Priority | Graphic Name | Functionality | Frequency | [7 empty] | ECB600 | 1
CHW Plant | Supply Water Temp |  |  |  |  | 1 |  |  |  |  | Chiller |  |  | HLI-SW-01 | 0 | HLI | Supply Water Temp | HLI | SW-01 | Chiller 1/2
CHW Plant | Return Water Temp |  |  |  |  | 1 | [7 empty] | HLI-SW-02 | 0 | HLI | Return Water Temp | HLI | SW-02 | Chiller 1/2
CHW Plant | Cooling demand |  |  |  |  | 1 | [7 empty] | HLI-SW-03 | 0 | HLI | Cooling demand | HLI | SW-03 | Chiller 1/2
CHW Plant | Setpoint |  |  |  |  | 1 | [7 empty] | HLI-SW-04 | 0 | HLI | Setpoint | HLI | SW-04 | Chiller 1/2
CHW Plant | Consumption |  |  |  |  | 1 | [7 empty] | HLI-SW-05 | 0 | HLI | Load Limiting | HLI | SW-05 | Chiller 1/2
CHW Plant | Faults |  |  |  |  | 1 | [7 empty] | HLI-SW-06 | 0 | HLI | Faults | HLI | SW-06 | Chiller 1/2 | -
CHW Plant | Current State |  |  |  |  | 1 | [7 empty] | HLI-SW-07 | 0 | HLI | Current State | HLI | SW-07 | Chiller 1/2 | -
CHW Plant | Current Load |  |  |  |  | 1 | [7 empty] | HLI-SW-08 | 0 | HLI | Current Load | HLI | SW-08 | Chiller 1/2 | -
CHW Plant | Load Limiting |  |  |  |  | 1 | [7 empty] | HLI-SW-09 | 0 | HLI | Load Limiting | HLI | SW-09 | Chiller 1/2
CHW Plant | Flow Status |  |  |  |  | 1 | [7 empty] | HLI-SW-10 | 0 | HLI | Flow Status | HLI | SW-10 | Chiller 1/2
CHW Plant | Head Pressure |  |  |  |  | 1 | [7 empty] | HLI-SW-11 | 0 | HLI | Head Pressure | HLI | SW-11 | Chiller 1/2
CHW Plant | Suction Pressure |  |  |  |  | 1 | [7 empty] | HLI-SW-12 | 0 | HLI | Suction Pressure | HLI | SW-12 | Chiller 1/2
CHW Plant | Energy Meter |  |  |  |  | 1 | [5 empty] | Display only | COV | Energy Meter-SW-13 | 0 | Energy Meter | Energy Meter | Energy Meter | SW-13 | Level-7 | Energy meter | 1
[8 empty] | Change Of State | 60s | Critical
CHW Plant | IO-DIM6-1 |  |  | 1 | [7 empty] | Display & Override | 10 Min or > 5% COV |  | 0 |  | IO-DIM6-1 |  | UI-1 |  | IO-DIM6 | 1
CHW Plant | CHW-PP-01 Status | 1 | [5 empty] | Change Of State | 60s | Critical |  |  |  | 0-UI-1 | 0 | 0 | CHW-PP-01 Status | 0 |  | Level-7 | SFS-1 | 1
CHW Plant | CHW-PP-02 Status | 1 | [5 empty] | Change Of State | 60s | Critical |  |  |  |  | 0 | 0 | CHW-PP-02 Status | 0 |  | Level-7 | SFS-1 | 1
CHW Plant | CHW-SP-01 Status | 1 | [5 empty] | Change Of State | 60s | Critical |  |  |  |  | 0 | 0 | CHW-SP-01 Status | 0 |  | Level-7 | SFS-1 | 1
CHW Plant | CHW-SP-02 Status | 1 | [5 empty] | Change Of State | 60s | Critical |  |  |  |  | 0 | 0 | CHW-SP-02 Status | 0 |  | Level-7 | SFS-1 | 1
CHW Plant | IO-DIM6-2 |  |  | 1 | [7 empty] | Display & Override | 10 Min or > 5% COV |  | 0 |  | IO-DIM6-2 |  | UI-2 |  | IO-DIM6 | 1
CHW Plant | CH1 Chiller Status | 1 | [5 empty] | Change Of State | 60s | Critical |  |  |  | 0- | 0 | 0 | CH1 Chiller Status | 0 |  | Level-7 | Terminals | 1
CHW Plant | CH2 Chiller Status | 1 | [5 empty] | Change Of State | 60s | Critical |  |  |  | 0- | 0 | 0 | CH2 Chiller Status | 0 |  | Level-7 | Terminals | 1
CHW Plant | CH1 Chiller General Fault | 1 | [5 empty] | Change Of State | 60s | Critical |  |  |  | 0- | 0 | 0 | CH1 Chiller General Fault | 0 |  | Level-7 | Terminals | 1
CHW Plant | CH2 Chiller General Fault | 1 | [5 empty] | Change Of State | 60s | Critical |  |  |  | 0- | 0 | 0 | CH2 Chiller General Fault | 0 |  | Level-7 | Terminals | 1
CHW Plant | Leak Detector CH1 |  |  | 1 | [7 empty] | Display only | COV | 0-UI-3 | 0 | 0 | Leak Detector CH1 | 0 | UI-3 | Level-7 | Terminals | 1
CHW Plant | Leak Detector CH2 |  |  | 1 | [7 empty] | Display only | COV | 0-UI-4 | 0 | 0 | Leak Detector CH2 | 0 | UI-4 | Level-7 | Terminals | 1
CHW Plant | Chiller 1 Evaporator DP |  |  | 1 |  |  |  | >or< Setpoint by 5% | 15min(1Hour Inhibit) | Critical |  | Display only | COV | 0-UI-5 | 0 | 0 | Chiller 1 Evaporator DP | 0 | UI-5 | Level-7 | QBE3000-D1 | 1
CHW Plant | Chiller 2 Evaporator DP |  |  | 1 |  |  |  | >or< Setpoint by 5% | 15min(1Hour Inhibit) | Critical |  | Display only | COV | 0-UI-6 | 0 | 0 | Chiller 2 Evaporator DP | 0 | UI-6 | Level-7 | QBE3000-D1 | 1
CHW Plant | System DP |  |  | 1 |  |  |  | >or< Setpoint by 5% | 15min(1Hour Inhibit) | Critical |  | Display only | COV | 0-UI-7 | 0 | 0 | System DP | 0 | UI-7 | Level-7 | QBE3000-D4 | 1
CHW Plant | Secondary CHW Flow |  |  | 1 | [7 empty] | Display only | COV | 0-UI-8 | 0 | 0 | Secondary CHW Flow | 0 | UI-8 | Level-7 | Flow meter | 1
CHW Plant | Decoupler CHW Flow |  |  | 1 | [7 empty] | Display only | COV | 0-UI-9 | 0 | 0 | Decoupler CHW Flow | 0 | UI-9 | Level-7 | Flow meter | 1
CHW Plant | Secondary CHW Supply Temp |  |  | 1 | [7 empty] | Display only | COV | 0-UI-10 | 0 | 0 | Secondary CHW Supply Temp | 0 | UI-10 | Level-7 | PDIGR-TE200CE24C2E + well | 1
CHW Plant | Secondary CHW Return Temp |  |  | 1 | [7 empty] | Display only | COV | 0-UI-11 | 0 | 0 | Secondary CHW Return Temp | 0 | UI-11 | Level-7 | PDIGR-TE200CE24C2E + well | 1
CHW Plant | Decoupler CHW Temp |  |  | 1 | [7 empty] | Display only | COV | 0-UI-12 | 0 | 0 | Decoupler CHW Temp | 0 | UI-12 | Level-7 | PDIGR-TE200CE24C2E + well | 1
CHW Plant | Tank Low CHW Temp | 1 | [5 empty] | Change Of State | 60s | Critical |  |  |  | 0-UI-13 | 0 | 0 | Tank Low CHW Temp | 0 | UI-13 | Level-7 | PDIGR-TE200CE24C2E + well | 1
CHW Plant | Tank High CHW Temp | 1 | [5 empty] | Change Of State | 60s | Critical |  |  |  | 0-UI-14 | 0 | 0 | Tank High CHW Temp | 0 | UI-14 | Level-7 | PDIGR-TE200CE24C2E + well | 1
CHW Plant | Chiller 1 Condenser DP | 1 | [5 empty] | Change Of State | 60s | Critical |  |  |  | 0-UI-15 | 0 | 0 | Chiller 1 Condenser DP | 0 | UI-15 | Level-7 | QBE3000-D1 | 1
CHW Plant | Chiller 2 Condenser DP | 1 | [5 empty] | Change Of State | 60s | Critical |  |  |  | 0-UI-16 | 0 | 0 | Chiller 2 Condenser DP | 0 | UI-16 | Level-7 | QBE3000-D1 | 1
0
Chiller Plantroom | CH1 Chiller Enable |  | 1 | [8 empty] | Display and Override | COV | 0-UO-1 | 0 | 0 | CH1 Chiller Enable | 0 | UO-1 | Level-7 | 12VDC Relay | 1
Chiller Plantroom | CH2 Chiller Enable |  | 1 | [8 empty] | Display and Override | COV | 0-UO-2 | 0 | 0 | CH2 Chiller Enable | 0 | UO-2 | Level-7 | 12VDC Relay | 1
CHW Plant | CHW Bypass Valve |  |  |  | 1 | [6 empty] | Display only | COV | 0-UO-3 | 0 | 0 | CHW Bypass Valve | 0 | UO-3 | Level-7 | CHWV Actuator | 1
| Sub Total | 12 | 2 | 12 | 1 | 13 | 0
| CHW Plant Extension | DI | DO | AI | AO | HLI | Prog | Condition | Timing | Priority | Graphic Name | Functionality | Frequency | [7 empty] | ECX400 | 1
CW Plant | CW-P-01 Status | 1 | [11 empty] | 0-UI-1 | 0 | 0 | CW-P-01 Status | 0 | UI-1 | Level-7 | SFS-1 | 1
CW Plant | CW-P-02 Status | 1 | [11 empty] | 0-UI-2 | 0 | 0 | CW-P-02 Status | 0 | UI-2 | Level-7 | SFS-1 | 1
CW Plant | CT 1 Cell 1 Sump Temp |  |  | 1 | [7 empty] | Display only | COV | 0-UI-7 | 0 | 0 | CT 1 Cell 1 Sump Temp | 0 | UI-7 | Level-7 | PDIGR-TE200CE24C2E + well | 1
CW Plant | CT 1 Cell 2 Sump Temp |  |  | 1 | [7 empty] | Display only | COV | 0-UI-8 | 0 | 0 | CT 1 Cell 2 Sump Temp | 0 | UI-8 | Level-7 | PDIGR-TE200CE24C2E + well | 1
CW Plant | CT Common Leave Temp |  |  | 1 | [7 empty] | Display only | COV | 0-UI-9 | 0 | 0 | CT Common Leave Temp | 0 | UI-9 | Level-7 | PDIGR-TE200CE24C2E + well | 1
Cool Tower | CT1 Cell1 Enter CW Iso Valve |  |  |  | 1 |  |  | Change Of State | 60s | Critical |  | Display only | COV | 0-UO-1 | 0 | 0 | CT1 Cell1 Enter CW Iso Valve | 0 | UO-1 | Level-7 | CWV Actuator | 1
Cool Tower | CT1 Cell1 Leave CW Iso Valve |  |  |  | 1 |  |  | Change Of State | 60s | Critical |  | Display only | COV | 0-UO-2 | 0 | 0 | CT1 Cell1 Leave CW Iso Valve | 0 | UO-2 | Level-7 | CWV Actuator | 1
Cool Tower | CT1 Cell2 Enter CW Iso Valve |  |  |  | 1 |  |  | Change Of State | 60s | Critical |  | Display only | COV | 0-UO-3 | 0 | 0 | CT1 Cell2 Enter CW Iso Valve | 0 | UO-3 | Level-7 | CWV Actuator | 1
Cool Tower | CT1 Cell2 Leave CW Iso Valve |  |  |  | 1 |  |  | Change Of State | 60s | Critical |  | Display only | COV | 0-UO-4 | 0 | 0 | CT1 Cell2 Leave CW Iso Valve | 0 | UO-4 | Level-7 | CWV Actuator | 1
Cool Tower | CTs CW Bypass Valve |  |  |  | 1 |  |  | Change Of State | 60s | Critical |  | Display only | COV | 0-UO-5 | 0 | 0 | CTs CW Bypass Valve | 0 | UO-5 | Level-7 | CWV Actuator | 1
Note on W13: Mike Walsh: Actuator Part Number
Note on W14: Mike Walsh: Actuator Part Number
Note on W15: Mike Walsh: Actuator Part Number
Note on W16: Mike Walsh: Actuator Part Number
Note on W17: Mike Walsh: Actuator Part Number
Note on W19: Mike Walsh: Actuator Part Number
Note on W20: Mike Walsh: Actuator Part Number
Note on W21: Mike Walsh: Actuator Part Number
Note on W22: Mike Walsh: Actuator Part Number
Note on W23: Mike Walsh: Actuator Part Number
Note on W24: Mike Walsh: Actuator Part Number
Note on W25: Mike Walsh: Actuator Part Number
Note on W26: Mike Walsh: Actuator Part Number
Note on W27: Mike Walsh: Actuator Part Number
Note on W28: Mike Walsh: Actuator Part Number
Note on W31: Mike Walsh: Actuator Part Number
Note on W32: Mike Walsh: Actuator Part Number
Note on W33: Mike Walsh: Actuator Part Number
Note on W34: Mike Walsh: Actuator Part Number
Note on W35: Mike Walsh: Actuator Part Number
Note on W41: Mike Walsh: Actuator Part Number
Note on W42: Mike Walsh: Actuator Part Number
Note on W46: Mike Walsh: Actuator Part Number
Note on W50: Mike Walsh: Actuator Part Number
Note on W51: Mike Walsh: Actuator Part Number
Note on W55: Mike Walsh: Actuator Part Number
Note on W56: Mike Walsh: Actuator Part Number
Note on W57: Mike Walsh: Actuator Part Number
Note on W58: Mike Walsh: Actuator Part Number
Note on W59: Mike Walsh: Actuator Part Number

## Hardware
Part | Supplier | Qty | Termination |  | Application | Cable | Power Consumption (VA)
Veris |  | 0
CHWV Actuator | TBA | 42 |  |  |  | Shielded twisted 3 core (Electra 7303C)
CWV Actuator | TBA | 5 |  |  |  | Shielded twisted 3 core (Electra 7303C)
HHWV Actuator | TBA | 43 |  |  |  | Shielded twisted 3 core (Electra 7303C)
Enthalpy | Vasalia | 0
Vaccume Tx
PT-015 (WS) |  | 2 | Wet Switch
Pressure Tx
HD2XVCTK (T) | Veris | 0 | Signal orange, Com black | Duct temp & RH
HD2XVCTK (H) | Veris | 0 | Signal blue, Com black, 24VAC red | Duct temp & RH
HO3XVSTK | Veris | 0 | Blue Humidity, Com black, 24VAC red, Orange thermister | Duct temp & RH |  | Shielded twisted 3 core (Electra 7303C) and Shielded twisted pair (Electra 7301P)
PXPLX02C | Veris | 0 | Signal, Com, 24V terminals | Dry DP high range | Duct static
PXPXX02C | Veris | 0 | Signal, Com, 24V terminals | Dry DP high range | Duct static
PXPXX01C | Veris | 0 | Signal, Com, 24V terminals | Dry DP low range | Space & stair press
PWLX06C | Veris | 0 | Signal, Com, 24V terminals | Wet DP | Chiller dp | Shielded twisted 3 core (Electra 7303C)
PWLX08C | Veris | 0 | Signal, Com, 24V terminals | Wet DP | Differential Pressure | Shielded twisted 3 core (Electra 7303C)
HWX2XCTK (H) | Veris | 0 | Signal, Com, 24VAC terminals | Space RH & temp | ICU | Shielded twisted 3 core (Electra 7303C)
HWX2XCTK (T) | Veris | 0 | Signal , Com Terminals | Space RH & temp | ICU | Shielded twisted pair (Electra 7301P)
HD3XVCX | Veris | 0 | Signal blue, Com black, 24VAC red | Duct RH | RA RH | Shielded twisted 3 core (Electra 7303C)
H800 | Veris | 0 | Connect pair | Solid Core Fixed Trip |  | Shielded twisted pair (Electra 7301P)
H608 | Veris | 0 | Connect pair | Split Core Variable Trip |  | Shielded twisted pair (Electra 7301P)
H600 | Veris | 0 | Connect pair | Split Core Fixed trip |  | Shielded twisted pair (Electra 7301P)
H221 | Veris | 0 | White +, Black - | Slpit Core Amps |  | Shielded twisted pair (Electra 7301P)
H321 | - |  |  |  |  | Shielded twisted pair (Electra 7301P)
EPP102-LCD | - |  |  |  | Duct static | Shielded twisted 3 core (Electra 7303C) |  | PXPLX02C
EPP102 | Veris | 0 | Signal, Com, 24V terminals | Dry DP high range | Duct static | Shielded twisted 3 core (Electra 7303C) |  | PXPXX02C
EPP101-LCD | Veris | 0 | Signal, Com, 24V terminals | Dry DP low range | Space & stair press | Shielded twisted 3 core (Electra 7303C) |  | PXPLX01C
EPP101 | Veris | 0 | Signal, Com, 24V terminals | Dry DP low range | Space & stair press | Shielded twisted 3 core (Electra 7303C) |  | PXPXX01C
Wago
750-430 | Wago 8 Digital Input slots $141.47 | 750-430 | Wago 8 Digital Input slots $141.47 | DI Module 8 inputs
750-600 Wago End Module $33.26 | Wago End Module $33.26 | 750-600 Wago End Module $33.26 | Wago End Module $33.26 | DI Module Interface
Siemens
SSR Module | Siemens | 4 | Signal U1, Com M, 24VAC G |  |  | Shielded twisted 3 Pair (Electra 7303P)
Flow meter |  | 4
Energy meter |  | 1
QVM62.1 | Siemens | 2 | Signal U1, Com M, 24VAC G | Velocity sensor |  | Shielded twisted 3 Pair (Electra 7303P)
QFM2160 Temp | Siemens | 7 | Temp Signal U2, 24VAC G, Neutral GO | Combined OA and Hum Sensor |  | Shielded twisted 3 Pair (Electra 7303P) | 1
QFM2160 Humidity | Siemens | 8 | Humidity Signal U1 | Combined OA and Hum Sensor |  | Shielded twisted 3 Pair (Electra 7303P) | 1
AT-02-1110-0 | Siemens | 0 | Signal 4, 24VDC 3 | CO sensor
SQS65 | Siemens | 0 | Signal, Com, 24VAC terminals
SQX62 | Siemens | 0 | Signal, Com, 24VAC terminals |  |  | Shielded twisted 3 Pair (Electra 7303P)
SKB60 | Siemens | 0 | Signal, Com, 24VAC terminals
SSB61 | Siemens | 0 | Signal grey 8, Com black 2, 24VAC red 1 |  |  | 2 core AirCon Cable (Electra AC7502) and Shielded twisted pair (Electra 7301P) | 2
SSC61 | Siemens | 0 | Signal, Com, 24VAC terminals
SKC60 | Siemens | 0 | Signal, Com, 24VAC terminals
GPA161.1E | Siemens | 0 | Signal grey 8, Com black 2, 24VAC red 1
GDB161.1E | Siemens | 44 | Signal grey 8, Com black 2, 24VAC red 2 |  |  | Shielded twisted 3 Pair (Electra 7303P)
GQD161.1A | Siemens | 0
GMA161.1E | Siemens | 0
GMA321.1E | Siemens | 0
TBA CHW actuator | Siemens | 0 | Signal, Com, 24VAC terminals |  | CHW bypass
TBA HW actuator | Siemens | 0 | Signal, Com, 24VAC terminals |  | HW bypass
UA9 | Siemens | 0 |  |  |  | Shielded twisted pair (Electra 7301P)
WM271MRP | Siemens | 0 | Connect Pair | Water Meter |  | Shielded twisted pair (Electra 7301P)
SBTFDK.085U1018 | Siemens | 0 | Signal, Com, 24VAC terminals | Magflow Signal Converter |  | Shielded twisted 3 Pair (Electra 7303P)
GIB161.1E | Siemens | 0 | Signal grey 8, Com black 2, 24VAC red 1 | Damper Actuator |  | 2 core AirCon Cable (Electra AC7502) and Shielded twisted pair (Electra 7301P) | 6
GBB161.1E | Siemens | 0 | Signal grey 8, Com black 2, 24VAC red 1 | Damper Actuator |  | 2 core AirCon Cable (Electra AC7502) and Shielded twisted pair (Electra 7301P) | 4
QPM-2102 (CO2) | Siemens | 0 | CO2 Signal | Combined CO2 and VOC Sensor | Duct Sensor | Shielded twisted 3 Pair (Electra 7302P)
QPM-2102 (VOC) | Siemens | 0 | VOC Signal | Combined CO2 and VOC Sensor | Duct Sensor | Shielded twisted 3 Pair (Electra 7302P)
QBM2030-1U | Siemens | 8 | Stairwell Static Pressure | Duct Static Pressure | Stair Pressure | Shielded twisted 3 Pair (Electra 7302P)
QBM2030-5 | Siemens | 4 | Duct Static Pressure | Duct Static Pressure | Duct Sensor | Shielded twisted 3 Pair (Electra 7302P)
QBM2030-30 | Siemens | 0
QBE3000-D1 | Siemens | 6 | Signal, Com, 24VAC terminals | Water Diff Pressure sensor | 0-1bar | Shielded twisted 3 core (Electra 7303C)
QBE3000-D4 | Siemens | 2 | Signal, Com, 24VAC terminals | Water Diff Pressure sensor | 0-4bar | Shielded twisted 3 core (Electra 7303C)
QFA3160 | Siemens |  | space temp 10VDC, RH 10VDC | Combo sensor |  | Shielded twisted 3 core (Electra 7303C)
Schneider
WFS-25AB | TAC | 0 | N.O. & Com terminals
TS-6721-853 | TAC | 0 | Connect pair |  | Immersion Sensor | Shielded twisted pair (Electra 7301P)
SFS-1 | TAC | 10 | Comm Blue, NO Marrone | Water DP Switch |  | Shielded twisted pair (Electra 7301P)
0-047-0106-0 | TAC | 0 | 2 N.O. & 3 Com terminals | Filter status |  | Shielded twisted pair (Electra 7301P)
930.8 | - |  |  |  |  | Shielded twisted pair (Electra 7301P)
TSMN-57011-850 | - |  |  |  | Space temp | Shielded twisted pair (Electra 7301P)
TS-6721-850 | TAC | 0 | Connect pair |  | Duct temp | Shielded twisted pair (Electra 7301P)
MN-S2 | TAC | 0 | Connect pair |  | Space Temp | Shielded twisted pair (Electra 7301P)
MN-S1HT | TAC | 0 | Connect Pair |  | Space Temp & Humidity | Shielded twisted pair (Electra 7301P)
Belimo
TR24.SR | Belimo | 0 | Signal White Y, 24VAC Red 2, Comm Black 1 | Ball Valve Actuator |  | Shielded twisted 3 core (Electra 7303C)
KM 24-3 (Existing) | Belimo | 0 | Comm Black 1, White Open 2, Red Close 3 | VAV Damper Actuator |  | Shielded twisted 3 core (Electra 7303C)
AF24-SR | Belimo | 0 | Signal White 3, 24VAC Red 2, Comm Black 1 | Damper Actuator Spring Return |  | Shielded twisted 3 core (Electra 7303C)
SRU24-SR | Belimo | 0 | Signal White 3, 24VAC Red 2, Comm Black 1 | Ball Valve Actuator |  | Shielded twisted 3 core (Electra 7303C)
LRU24-SR | Belimo | 0 | Signal White 3, 24VAC Red 2, Comm Black 1 | Ball Valve Actuator |  | Shielded twisted 3 core (Electra 7303C)
Honeywell
Actuator Terminals | Honeywell |  | Signal - F, Comm - T2 |  |  | Shielded twisted pair (Electra 7301P) | 1.8
ML7421B1023-E | Honeywell | 0 | Signal - Plus, 24VAC - T1, Comm - T2 |  |  | Shielded twisted 3 core (Electra 7303C) | 7
M7410E1002 | Honeywell | 0 | Signal - Green, 24VAC - Brown, Comm - White | Valve Actuator |  | Shielded twisted 3 core (Electra 7303C)
ML7420A6033-E | Honeywell | 0 | Signal - Plus, Signal Com - Minus, 24VAC - T1, Comm - T2 | Valve Actuator |  | Shielded twisted 3 core (Electra 7303C)
CS7510A2008 | -
CS7520A2007 | -
Dwyer
CCS | Dwyer | 41 | -46 | Current Switch |  | Shielded twisted pair (Electra 7301P)
GSTA | Dwyer | 0 | Signal White 3, 24VAC Red 2, Comm Black 4 | CO Sensor |  | Shielded twisted 3 core (Electra 7303C)
CDW | Dwyer | 0 | Signal White 2, 24VAC Red 3, Comm Black 1 | CO2 Sensor |  | Shielded twisted 3 core (Electra 7303C)
CDD | Dwyer | 0 | Signal White 2, 24VAC Red 3, Comm Black 2 | CO2 Sensor |  | Shielded twisted 3 core (Electra 7303C)
AFS - 930.80222524 | Dwyer | 52 | white = signal, black = Common | 0-500Pa Air Switch | Fan Status | 1 pair 7/0.30 shielded twisted cable (Electra 7301p)
Other
12VDC Relay |  | 27 | Terminals in MSSB |  |  | Panel Wire
24VAC Relay |  | 40 | Terminals in MSSB |  |  | Panel Wire
Lighting 24VAC Relay |  | 0 | Terminals in DB |  |  | Shielded twisted pair (Electra 7301P)
Terminals |  | 57 | Terminals in MSSB |  |  | Shielded twisted pair (Electra 7301P)
VSD Terminals |  | 0 | Terminals in VSD |  |  | Shielded twisted pair (Electra 7301P)
Lift Terminals |  | 2 | Terminals in Lift |  |  | Shielded twisted pair (Electra 7301P)
Walkway Terminals |  | 0 | Terminals in Walkway |  |  | Shielded twisted pair (Electra 7301P)
AHU Terminals |  | 0 | Terminals in AHU Controller |  |  | Shielded twisted pair (Electra 7301P)
FCU Terminals |  | 0 | Terminals in FCU |  |  | Shielded twisted pair (Electra 7301P)
IO-RM3 | - | 0 | RM3 3 Relay Module |  |  | Shielded twisted pair (Electra 7301P)
HWH Terminals | - | 0 | Terminals in HWH |  |  | Shielded twisted pair (Electra 7301P)
Unit Terminals |  | 0 | Terminals in Unit |  |  | Shielded twisted pair (Electra 7301P)
IO-DIM6 | Sontay | 38 | DIM6 Input Multiplexer |  |  | Shielded twisted pair (Electra 7301P)
Pushbutton |  | 0 | Connect Pair |  |  | Shielded twisted pair (Electra 7301P)
Green Neon |  | 0 | Switched 24VAC |  |  | 2 core AirCon Cable (Electra AC7502)
Rocker Switch |  | 0 | Connect Pair |  |  | Shielded twisted pair (Electra 7301P)
0-10VDC Relay |  | 0 | Signal White +, Signal Comm Black - across coil |  |  | Shielded twisted pair (Electra 7301P)
07KIT-RELAYUNDI | Distech | 0 | Distech UO Relay |  |  | Shielded twisted pair (Electra 7301P)
MA-0-1110-A-8 | MSR | 0 | CO Car Park Sensor
Existing Temperature |  | 0 | Connect pair | Existing Sensor |  | Shielded twisted pair (Electra 7301P) | 1
CDD | Dwyer | 0 | Signal, Com, 24VAC terminals | CO2 Sensor | Duct Sensor | Shielded twisted 3 core (Electra 7303C)
TE-702-B-12-C | Mamac | 0 | Connect pair |  | Duct temp | Shielded twisted pair (Electra 7301P)
TBA |  | 0 | To Be Advised | To Be Advised | To Be Advised | To Be Advised
Motion Detector (OC-C-LV) | Sontay | 0 | To Be Advised | To Be Advised | To Be Advised | To Be Advised
QLS60 Siemens Solar glare
GAS-CO2-0xx-A | Gas Alarm | 0 | Signal, Com, 24VAC terminals | CO2 Sensor | Wall Sensor | Shielded twisted 3 core (Electra 7303C)
Distech
EC-Sensor | [5 empty] | 1 pair 7/0.30 shielded twisted cable (Electra 7301p)
EC-Smart-Vue | Distech | 0 | RJ45 Plug - terminate using TIA/EIA-568-A | Communicating Sensor |  | Cat5e Cable daisy chained between each sensor and controller
PDIGR-TE200CE24B2E | Distech | 0 | white = signal, black = Common | Immersion Pipe Sensor |  | 1 pair 7/0.30 shielded twisted cable (Electra 7301p)
PDIGR-TE200BE24B2 | Distech | 78 | white = signal, black = Common | Immersion Pipe Sensor |  | 1 pair 7/0.30 shielded twisted cable (Electra 7301p)
PDIGR-AFS-262-112 | Distech | 0 | white = signal, black = Common | 0-500Pa Air Switch | Filter Status | 1 pair 7/0.30 shielded twisted cable (Electra 7301p)
PDIGR-WP-D-111-LCD | Distech | 0 | red = 24VAC, white = 0-10VDC, black = Common | 0-100, 200, 500 & 1000kPa Wet Pressure with LCD | ChW/HW Loop Pressure | 3 core 7/0.30 shielded twisted cable (Electra 7303C)
PDIGR-CDD1A4000-T24 | Distech | 0 | red = 24VAC, white = 0-10VDC, black = Common & white = signal, black = common | Wall Mount CO2 & Temp | Space CO2 & Temp | 3 core 7/0.30 shielded twisted cable (Electra 7303C) & 1 pair 7/030 shielded twisted cable (Electra 7301p)
PDIGR-LP2B06S | Distech | 0 | red = 24VAC, white = 0-10VDC, black = Common | 0-500. 1000Pa Air Pressure Sensor with LCD and static pickup | Static Pressure | 3 core 7/0.30 shielded twisted cable (Electra 7303C)
PDIGR-TE200BE24D2 | Distech | 0 | white = signal, black = Common | Duct Mount, 200mm Sensor | Duct Temp | 1 pair 7/0.30 shielded twisted cable (Electra 7301p)
PDIGR-IE200BE24D2 | Distech | 0 | white = signal, black = Common | Duct Mount, 200mm Sensor | Duct Temp | 1 pair 7/0.30 shielded twisted cable (Electra 7301p)
PDITE-SENSORX0 | Distech | 27 | white = signal, black = Common | Temperature |  | 1 pair 7/0.30 shielded twisted cable (Electra 7301p)
PDIGR-TE200BE24B2 + well | Distech | 1 | white = signal, black = Common | Temperature |  | 2 pair 7/0.30 shielded twisted cable (Electra 7301p)
E1210 | MOXA | 0
PDIGR-TE200FDB24A | Distech | 4 | white = signal, black = Common | Duct Mount averaging 1.8 m | Duct Temp Averaging | 1 pair 7/0.30 shielded twisted cable (Electra 7301p)
PDIGR-TE200CE24C2E + well | Distech | 15 | white = signal, black = Common | Immersion Temperature |  | 2 pair 7/0.30 shielded twisted cable (Electra 7301p)
Software Point |  | 37 | - | - | - | -
Limit of dropdown list |  | 0
ECB103 |  | 0
ECB203 |  | 26
ECB300 |  | 6
ECB400 |  | 1
ECB600 |  | 13
ECX420 |  | 3
ECX400 |  | 1
VAVO |  | 0
VAVS |  | 0
VAV |  | 0
ECB600 + ECX400 |  | 0
Modulating Actuator Terminal | CO2 Sensor | 0 |  | 1 | Damper Control | Shielded twisted 3 Pair (Electra 7303P) |  |  | RA Duct Work | 1
VSD Terminal | VOC Sensor | 0 |  | 1 | Fan Speed Control | 1 pair 7/0.30 shielded twisted cable (Electra 7301p) |  |  | RA Duct Work
- | - | 0 | - | - | - | -
UPS Terminals |  | 0
Fire Relay |  | 0
0
SSA61 |  | 0
SSD61 |  | 0
SQD65 |  | 0
SAX61 |  | 0
STA63 |  | 0
Limit of dropdown list
Immersion
Temp with PB
PC
SSR
Door Reed Switch
Flow Meters
VSDs
Smoke Dampers